## Slab_Properties
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span
l2 = | 34 | ft | interior
l1 / l2 = | 1 |  | * must be < 2.0
c1 = | 32 | in
c2 = | 32 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 18 | in
d = | 16.75 | in
wc = | 150 | pcf
yt = | 9 | in
n = | 5.6374
lcw = | 1
fr = | 318.1981 | psi
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 225 | psf
mass = | 8472.5466 | lb sec2/ft
weight = | 272.816 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 398 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1660.6771 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1660.6771 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 863.5521 | k-ft
M1n1u = | 431.776 | k-ft
M1n2u = | 1162.474 | k-ft
M2pu = | 581.237 | k-ft
M2n1u = | 1079.4401 | k-ft
M2n2u = | 1079.4401 | k-ft
Service Moments
M01,DL = | 938.825 | k-ft | *includes SDL and self-weight
M01,LL = | 333.8044 | k-ft
M02,DL = | 938.825 | k-ft
M02,LL = | 333.8044 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 292.9134 | 195.2756 | k-ft
l1 | DL | n1 | 244.0945 | 0 | k-ft
l1 | DL | n2 | 492.8831 | 152.5591 | k-ft
l1 | LL | p | 104.147 | 69.4313 | k-ft
l1 | LL | n1 | 86.7892 | 0 | k-ft
l1 | LL | n2 | 175.2473 | 58.4158 | k-ft
l2 | DL | p | 197.1532 | 131.4355 | k-ft
l2 | DL | n1 | 457.6772 | 152.5591 | k-ft
l2 | DL | n2 | 457.6772 | 152.5591 | k-ft
l2 | LL | p | 70.0989 | 46.7326 | k-ft
l2 | LL | n1 | 162.7297 | 54.2432 | k-ft
l2 | LL | n2 | 162.7297 | 54.2432 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 518.1313 | 345.4208 | k-ft
l1 | n1 | 431.776 | 0 | k-ft
l1 | n2 | 871.8555 | 276.5361 | k-ft
l2 | p | 348.7422 | 232.4948 | k-ft
l2 | n1 | 809.5801 | 269.86 | k-ft
l2 | n2 | 809.5801 | 269.86 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation: |  |  |  |  | User input:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Column | Middle
l1 | p | 8.5425 | 8.5425 | in2 | l1 | p | 8.5425 | 8.5425 | in2
l1 | n1 | 8.5425 | 8.5425 | in2 | l1 | n1 | 8.5425 | 8.5425 | in2
l1 | n2 | 9.8319 | 8.5425 | in2 | l1 | n2 | 9.8319 | 8.5425 | in2
l2 | p | 8.5425 | 8.5425 | in2 | l2 | p | 8.5425 | 8.5425 | in2
l2 | n1 | 9.1296 | 8.5425 | in2 | l2 | n1 | 9.1296 | 8.5425 | in2
l2 | n2 | 9.1296 | 8.5425 | in2 | l2 | n2 | 9.1296 | 8.5425 | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 99144 | 99144 | in3
l1 | n1 | 99144 | 99144 | in3
l1 | n2 | 99144 | 99144 | in3
l2 | p | 99144 | 99144 | in3
l2 | n1 | 99144 | 99144 | in3
l2 | n2 | 99144 | 99144 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 20923.5793 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.73567 | 1.1035 | 0.03 | 0.03
l1 | n1 | 35434.0914 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.88281 | 1.1 | 0.03 | 0.03
l1 | n2 | 14747.5382 | 99144 | in3 | 3.6806 | 4.2361 | 2.7574 | 2.586 | 12277.7365 | 10837.3136 | 292.1058 | 292.1058 | 0.4372 | 1.3846 | 0.034528 | 0.03
l2 | p | 99144 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 1.093 | 1.6395 | 0.03 | 0.03
l2 | n1 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
l2 | n2 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 22173.75 | 99144 | in3
l2 | 73690.781 | 99144 | in3
Calculate Panel Ie
Iep = | 121317.75 | in3
Calculate Panel Ig
Igp = | 198288 | in3
Calculate k1
k1 = | 0.61183
Calculate fi |  |  | Interp li2
k2 = | 2.1 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 7.3292 | slug / ft2 | 2 | 9.29
fi = | 8.7619 | Hz
Calculate/Input Parameters for DG11
W = | 272816 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits
fn= | 8.7619 | Hz
W = | 272816 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips
Very Slow | 8.7619 | 1.25 | [5 empty] | 656.1208 |  | 656.1208 |  | 656.1208 | mips
Slow | 8.7619 | 1.6 | 6.8 | 6 | 8 | 0.1 | 2255.7196 | 1078.8285 | 3592.9892 | 1216.1941 | N/A | 1078.8285 | mips | * does not consider mode scaling
Moderate | 8.7619 | 1.85 | 8 | 7 | 9 | 0.09 | 2462.2805 | 1429.2044 | 3228.1498 | 1380.8096 | 1600.7426 | 1600.7426 | mips
Fast | 8.7619 | 2.1 | 8.8 | 8 | 10 | 0.08 | 2687.7567 | 1815.3443 | 2989.6115 | 1537.3001 | 2436.3591 | 2436.3591 | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26404 | 3.4321 | 186.116 | 0.03 | 3382 | 12010 | 12430 | 12863
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.2769 | 3.8847 | 186.116 | 0.03 | 2972 | 10796 | 11223 | 11667
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29152 | 3.9859 | 186.116 | 0.03 | 2884 | 10529 | 10958 | 11404
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.3093 | 4.1057 | 186.116 | 0.03 | 2794 | 10251 | 10681 | 11129
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33328 | 4.2618 | 186.116 | 0.03 | 2688 | 9919 | 10350 | 10801
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.03 | 2083 | 7872 | 8276 | 8702
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47936 | 5.5517 | 200.566 | 0.03 | 1853 | 7086 | 7490 | 7918
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48247 | 5.5697 | 200.566 | 0.03 | 1845 | 7059 | 7464 | 7891
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48586 | 5.5892 | 200.566 | 0.03 | 1837 | 7032 | 7437 | 7864
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.4902 | 5.6141 | 200.566 | 0.03 | 1830 | 7006 | 7410 | 7838
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53456 | 5.7253 | 215.016 | 0.03 | 1665 | 6391 | 6768 | 7167
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.5514 | 6.4269 | 215.016 | 0.03 | 1452 | 5150 | 5999 | 6397
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.57369 | 6.5555 | 215.016 | 0.03 | 1417 | 4869 | 5870 | 6268
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57362 | 6.5551 | 215.016 | 0.03 | 1417 | 4869 | 5870 | 6268
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.5736 | 6.555 | 215.016 | 0.03 | 1420 | 4890 | 5880 | 6278
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57675 | 6.3843 | 229.466 | 0.03 | 1373 | 4926 | 5667 | 6040
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57726 | 7.0595 | 229.466 | 0.03 | 1213 | 3549 | 5019 | 5438
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57782 | 7.0629 | 229.466 | 0.03 | 1213 | 3549 | 5019 | 5438
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.5784 | 7.0665 | 229.466 | 0.03 | 1211 | 3528 | 5003 | 5430
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57902 | 7.0703 | 229.466 | 0.03 | 1211 | 3528 | 5003 | 5430
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58291 | 6.8581 | 243.916 | 0.03 | 1183 | 3720 | 4925 | 5275
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58371 | 7.5852 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58456 | 7.5907 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58545 | 7.5966 | 243.916 | 0.03 | 1041 | 2309 | 3895 | 4723
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58641 | 7.6028 | 243.916 | 0.03 | 1041 | 2309 | 3895 | 4723
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59118 | 7.3496 | 258.366 | 0.03 | 1025 | 2630 | 4038 | 4625
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59241 | 8.1316 | 258.366 | 0.03 | 902 | 1433 | 2911 | 4055
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.5937 | 8.1405 | 258.366 | 0.03 | 900 | 1431 | 2897 | 4043
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59512 | 8.1502 | 258.366 | 0.03 | 899 | 1428 | 2882 | 4031
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59668 | 8.1608 | 258.366 | 0.03 | 897 | 1426 | 2868 | 4019
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60273 | 7.8683 | 272.816 | 0.03 | 890 | 1605 | 3113 | 4061
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60472 | 8.7109 | 272.816 | 0.03 | 781 | 1248 | 1963 | 3189
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60687 | 8.7263 | 272.816 | 0.03 | 778 | 1245 | 1936 | 3166
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60923 | 8.7433 | 272.816 | 0.03 | 777 | 1243 | 1922 | 3155
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61182 | 8.7618 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133

## Rho_25%nonmin
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | % Change from Default rho
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00419 | 0.00349 | 0.00705 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00654 | 0.00654 | 0.0025 | 0.0025 | 0.0025 | 0.28013 | 3.5351 | 186.116 | 0.03 | 3273 | 11693 | 12114 | 12551 | -0.032229 | -0.026395 | -0.025422 | -0.024256
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00415 | 0.00345 | 0.00698 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00647 | 0.00647 | 0.0025 | 0.0025 | 0.0025 | 0.293 | 3.996 | 186.116 | 0.03 | 2877 | 10506 | 10934 | 11381 | -0.031965 | -0.026862 | -0.025751 | -0.024514
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0041 | 0.00342 | 0.0069 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00641 | 0.00641 | 0.0025 | 0.0025 | 0.0025 | 0.30745 | 4.0933 | 186.116 | 0.03 | 2809 | 10296 | 10726 | 11174 | -0.026006 | -0.022129 | -0.021172 | -0.020168
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00338 | 0.00682 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00635 | 0.00635 | 0.0025 | 0.0025 | 0.0025 | 0.32521 | 4.2099 | 186.116 | 0.03 | 2722 | 10027 | 10459 | 10908 | -0.02577 | -0.021852 | -0.020785 | -0.019858
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00401 | 0.00335 | 0.00675 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00628 | 0.00628 | 0.0025 | 0.0025 | 0.0025 | 0.34909 | 4.3617 | 186.116 | 0.03 | 2621 | 9707 | 10139 | 10591 | -0.024926 | -0.021373 | -0.020386 | -0.019443
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00367 | 0.0025 | 0.00619 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00575 | 0.00575 | 0.0025 | 0.0025 | 0.0025 | 0.49004 | 5.0786 | 200.566 | 0.03 | 2051 | 7763 | 8168 | 8593 | -0.015362 | -0.013847 | -0.01305 | -0.012526
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00364 | 0.0025 | 0.00613 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00569 | 0.00569 | 0.0025 | 0.0025 | 0.0025 | 0.49262 | 5.628 | 200.566 | 0.03 | 1822 | 6979 | 7384 | 7811 | -0.01673 | -0.0151 | -0.014152 | -0.013514
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036 | 0.0025 | 0.00606 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00562 | 0.00562 | 0.0025 | 0.0025 | 0.0025 | 0.49567 | 5.6454 | 200.566 | 0.03 | 1815 | 6953 | 7357 | 7785 | -0.01626 | -0.015016 | -0.014335 | -0.013433
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00356 | 0.0025 | 0.006 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00558 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.49905 | 5.6646 | 200.566 | 0.03 | 1811 | 6940 | 7344 | 7772 | -0.014154 | -0.013083 | -0.012505 | -0.011699
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00352 | 0.0025 | 0.00593 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00551 | 0.00551 | 0.0025 | 0.0025 | 0.0025 | 0.50331 | 5.6887 | 200.566 | 0.03 | 1800 | 6901 | 7305 | 7733 | -0.016393 | -0.014987 | -0.01417 | -0.013396
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00326 | 0.0025 | 0.0055 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0051 | 0.0051 | 0.0025 | 0.0025 | 0.0025 | 0.54741 | 5.7937 | 215.016 | 0.03 | 1645 | 6319 | 6696 | 7095 | -0.012012 | -0.011266 | -0.010638 | -0.010046
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00324 | 0.0025 | 0.00544 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00505 | 0.00505 | 0.0025 | 0.0025 | 0.0025 | 0.56433 | 6.5018 | 215.016 | 0.03 | 1433 | 4998 | 5929 | 6327 | -0.013085 | -0.029515 | -0.011669 | -0.010943
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032 | 0.0025 | 0.00539 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005 | 0.005 | 0.0025 | 0.0025 | 0.0025 | 0.58653 | 6.6285 | 215.016 | 0.03 | 1399 | 4717 | 5802 | 6200 | -0.012703 | -0.031218 | -0.011584 | -0.010849
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00316 | 0.0025 | 0.00532 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00495 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.58635 | 6.6274 | 215.016 | 0.03 | 1399 | 4717 | 5802 | 6200 | -0.012703 | -0.031218 | -0.011584 | -0.010849
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.0025 | 0.00528 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0049 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.58642 | 6.6279 | 215.016 | 0.03 | 1399 | 4717 | 5802 | 6200 | -0.014789 | -0.035378 | -0.013265 | -0.012424
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00494 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00459 | 0.00459 | 0.0025 | 0.0025 | 0.0025 | 0.57943 | 6.3992 | 229.466 | 0.03 | 1368 | 4885 | 5648 | 6021 | -0.0036417 | -0.0083232 | -0.0033527 | -0.0031457
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00489 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00454 | 0.00454 | 0.0025 | 0.0025 | 0.0025 | 0.57994 | 7.0758 | 229.466 | 0.03 | 1209 | 3508 | 4987 | 5422 | -0.0032976 | -0.011553 | -0.0063758 | -0.0029423
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00484 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00449 | 0.00449 | 0.0025 | 0.0025 | 0.0025 | 0.58047 | 7.0791 | 229.466 | 0.03 | 1209 | 3508 | 4987 | 5422 | -0.0032976 | -0.011553 | -0.0063758 | -0.0029423
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00479 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00444 | 0.00444 | 0.0025 | 0.0025 | 0.0025 | 0.58104 | 7.0826 | 229.466 | 0.03 | 1209 | 3508 | 4987 | 5422 | -0.0016515 | -0.0056689 | -0.0031981 | -0.0014733
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0044 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.58165 | 7.0863 | 229.466 | 0.03 | 1207 | 3488 | 4971 | 5414 | -0.0033031 | -0.011338 | -0.0063962 | -0.0029466
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00447 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00415 | 0.00415 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 6.8733 | 243.916 | 0.03 | 1181 | 3701 | 4917 | 5267 | -0.0016906 | -0.0051075 | -0.0016244 | -0.0015166
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00443 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00411 | 0.00411 | 0.0025 | 0.0025 | 0.0025 | 0.58626 | 7.6018 | 243.916 | 0.03 | 1041 | 2309 | 3895 | 4723 | -0.0019175 | -0.0081615 | -0.004091 | -0.0014799
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00438 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00406 | 0.00406 | 0.0025 | 0.0025 | 0.0025 | 0.58709 | 7.6071 | 243.916 | 0.03 | 1039 | 2290 | 3880 | 4716 | -0.0038351 | -0.016323 | -0.0079264 | -0.0029598
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00434 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00402 | 0.00402 | 0.0025 | 0.0025 | 0.0025 | 0.58799 | 7.613 | 243.916 | 0.03 | 1039 | 2290 | 3880 | 4716 | -0.0019212 | -0.0082287 | -0.0038511 | -0.0014821
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00429 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00399 | 0.00399 | 0.0025 | 0.0025 | 0.0025 | 0.58892 | 7.619 | 243.916 | 0.03 | 1038 | 2271 | 3865 | 4710 | -0.0028818 | -0.016457 | -0.0077022 | -0.0027525
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00409 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00379 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.59367 | 7.365 | 258.366 | 0.03 | 1023 | 2612 | 4024 | 4618 | -0.0019512 | -0.0068441 | -0.0034671 | -0.0015135
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00375 | 0.00375 | 0.0025 | 0.0025 | 0.0025 | 0.59486 | 8.1484 | 258.366 | 0.03 | 899 | 1428 | 2882 | 4031 | -0.0033259 | -0.0034892 | -0.0099622 | -0.0059186
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00371 | 0.00371 | 0.0025 | 0.0025 | 0.0025 | 0.59615 | 8.1573 | 258.366 | 0.03 | 897 | 1426 | 2868 | 4019 | -0.0033333 | -0.0034941 | -0.01001 | -0.0059362
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.59757 | 8.167 | 258.366 | 0.03 | 896 | 1424 | 2853 | 4007 | -0.003337 | -0.0028011 | -0.010062 | -0.0059539
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00364 | 0.00364 | 0.0025 | 0.0025 | 0.0025 | 0.5991 | 8.1774 | 258.366 | 0.03 | 894 | 1422 | 2839 | 3996 | -0.0033445 | -0.002805 | -0.010112 | -0.0057228
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00349 | 0.00349 | 0.0025 | 0.0025 | 0.0025 | 0.60512 | 7.8838 | 272.816 | 0.03 | 889 | 1588 | 3099 | 4055 | -0.0011236 | -0.010592 | -0.0044973 | -0.0014775
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00371 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00345 | 0.00345 | 0.0025 | 0.0025 | 0.0025 | 0.60711 | 8.728 | 272.816 | 0.03 | 778 | 1245 | 1936 | 3166 | -0.0038412 | -0.0024038 | -0.013754 | -0.0072123
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00341 | 0.00341 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7434 | 272.816 | 0.03 | 777 | 1243 | 1922 | 3155 | -0.0012853 | -0.0016064 | -0.0072314 | -0.0034744
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00364 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00338 | 0.00338 | 0.0025 | 0.0025 | 0.0025 | 0.6116 | 8.7603 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133 | -0.002574 | -0.003218 | -0.014048 | -0.0069731
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0036 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00334 | 0.00334 | 0.0025 | 0.0025 | 0.0025 | 0.61418 | 8.7788 | 272.816 | 0.03 | 772 | 1236 | 1867 | 3110 | -0.003871 | -0.0024213 | -0.014776 | -0.0073412

## Rho_50%nonmin
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | % Change from Default rho
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00418 | 0.00846 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00785 | 0.00785 | 0.0025 | 0.0025 | 0.0025 | 0.29533 | 3.6298 | 186.116 | 0.03 | 3188 | 11444 | 11867 | 12305 | -0.057363 | -0.047127 | -0.045294 | -0.04338
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00414 | 0.00837 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00777 | 0.00777 | 0.0025 | 0.0025 | 0.0025 | 0.30814 | 4.0979 | 186.116 | 0.03 | 2801 | 10273 | 10703 | 11151 | -0.057537 | -0.048444 | -0.046333 | -0.044227
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00411 | 0.00828 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0077 | 0.0077 | 0.0025 | 0.0025 | 0.0025 | 0.3225 | 4.1923 | 186.116 | 0.03 | 2736 | 10071 | 10502 | 10952 | -0.051318 | -0.043499 | -0.041613 | -0.039635
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00819 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00762 | 0.00762 | 0.0025 | 0.0025 | 0.0025 | 0.34019 | 4.3058 | 186.116 | 0.03 | 2654 | 9812 | 10244 | 10695 | -0.050107 | -0.042825 | -0.040914 | -0.038997
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00481 | 0.00402 | 0.0081 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00753 | 0.00753 | 0.0025 | 0.0025 | 0.0025 | 0.36399 | 4.4539 | 186.116 | 0.03 | 2563 | 9522 | 9955 | 10408 | -0.046503 | -0.040024 | -0.038164 | -0.036386
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.0025 | 0.00743 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0069 | 0.0069 | 0.0025 | 0.0025 | 0.0025 | 0.50266 | 5.1436 | 200.566 | 0.03 | 2024 | 7671 | 8076 | 8502 | -0.028325 | -0.025534 | -0.024166 | -0.022983
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00436 | 0.0025 | 0.00735 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00683 | 0.00683 | 0.0025 | 0.0025 | 0.0025 | 0.50519 | 5.6993 | 200.566 | 0.03 | 1796 | 6888 | 7292 | 7720 | -0.030761 | -0.027942 | -0.026435 | -0.025006
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.0025 | 0.00728 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00675 | 0.00675 | 0.0025 | 0.0025 | 0.0025 | 0.50818 | 5.7162 | 200.566 | 0.03 | 1789 | 6862 | 7266 | 7694 | -0.030352 | -0.027908 | -0.026527 | -0.024965
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00428 | 0.0025 | 0.0072 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00669 | 0.00669 | 0.0025 | 0.0025 | 0.0025 | 0.51151 | 5.7349 | 200.566 | 0.03 | 1785 | 6849 | 7253 | 7681 | -0.028307 | -0.026024 | -0.024741 | -0.023271
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00423 | 0.0025 | 0.00711 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00661 | 0.00661 | 0.0025 | 0.0025 | 0.0025 | 0.51572 | 5.7584 | 200.566 | 0.03 | 1774 | 6811 | 7215 | 7643 | -0.030601 | -0.027833 | -0.026316 | -0.024879
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.0025 | 0.0066 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00612 | 0.00612 | 0.0025 | 0.0025 | 0.0025 | 0.55964 | 5.8581 | 215.016 | 0.03 | 1622 | 6238 | 6614 | 7013 | -0.025826 | -0.02394 | -0.022754 | -0.021487
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00388 | 0.0025 | 0.00652 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00606 | 0.00606 | 0.0025 | 0.0025 | 0.0025 | 0.57652 | 6.5717 | 215.016 | 0.03 | 1415 | 4847 | 5860 | 6258 | -0.025482 | -0.058835 | -0.023171 | -0.021729
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00384 | 0.0025 | 0.00647 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006 | 0.006 | 0.0025 | 0.0025 | 0.0025 | 0.59868 | 6.6968 | 215.016 | 0.03 | 1381 | 4566 | 5735 | 6133 | -0.025406 | -0.06223 | -0.022998 | -0.021538
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0038 | 0.0025 | 0.00639 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00594 | 0.00594 | 0.0025 | 0.0025 | 0.0025 | 0.59845 | 6.6955 | 215.016 | 0.03 | 1381 | 4566 | 5735 | 6133 | -0.025406 | -0.06223 | -0.022998 | -0.021538
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00377 | 0.0025 | 0.00633 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00588 | 0.00588 | 0.0025 | 0.0025 | 0.0025 | 0.59851 | 6.6958 | 215.016 | 0.03 | 1381 | 4566 | 5735 | 6133 | -0.027465 | -0.066258 | -0.02466 | -0.023097
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00593 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0055 | 0.0055 | 0.0025 | 0.0025 | 0.0025 | 0.58195 | 6.413 | 229.466 | 0.03 | 1366 | 4865 | 5638 | 6012 | -0.0050983 | -0.012383 | -0.0051173 | -0.0046358
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00587 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00545 | 0.00545 | 0.0025 | 0.0025 | 0.0025 | 0.58244 | 7.0911 | 229.466 | 0.03 | 1207 | 3488 | 4971 | 5414 | -0.0049464 | -0.017188 | -0.0095637 | -0.0044134
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00581 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00539 | 0.00539 | 0.0025 | 0.0025 | 0.0025 | 0.58296 | 7.0943 | 229.466 | 0.03 | 1207 | 3488 | 4971 | 5414 | -0.0049464 | -0.017188 | -0.0095637 | -0.0044134
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00575 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00533 | 0.00533 | 0.0025 | 0.0025 | 0.0025 | 0.58351 | 7.0976 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405 | -0.0049546 | -0.017007 | -0.0097941 | -0.0046041
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00568 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00528 | 0.00528 | 0.0025 | 0.0025 | 0.0025 | 0.58411 | 7.1013 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405 | -0.0049546 | -0.017007 | -0.0097941 | -0.0046041
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00537 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00498 | 0.00498 | 0.0025 | 0.0025 | 0.0025 | 0.5879 | 6.8874 | 243.916 | 0.03 | 1177 | 3663 | 4901 | 5251 | -0.0050719 | -0.015323 | -0.0048731 | -0.0045498
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00531 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00493 | 0.00493 | 0.0025 | 0.0025 | 0.0025 | 0.58866 | 7.6173 | 243.916 | 0.03 | 1038 | 2271 | 3865 | 4710 | -0.0047939 | -0.024485 | -0.011762 | -0.0042283
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00525 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00487 | 0.00487 | 0.0025 | 0.0025 | 0.0025 | 0.58947 | 7.6226 | 243.916 | 0.03 | 1038 | 2271 | 3865 | 4710 | -0.0047939 | -0.024485 | -0.011762 | -0.0042283
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0052 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00483 | 0.00483 | 0.0025 | 0.0025 | 0.0025 | 0.59037 | 7.6284 | 243.916 | 0.03 | 1036 | 2252 | 3849 | 4703 | -0.0048031 | -0.024686 | -0.01181 | -0.0042346
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00514 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00479 | 0.00479 | 0.0025 | 0.0025 | 0.0025 | 0.59128 | 7.6343 | 243.916 | 0.03 | 1036 | 2252 | 3849 | 4703 | -0.0048031 | -0.024686 | -0.01181 | -0.0042346
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.596 | 7.3794 | 258.366 | 0.03 | 1020 | 2576 | 3995 | 4605 | -0.004878 | -0.020532 | -0.010649 | -0.0043243
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00484 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.59717 | 8.1642 | 258.366 | 0.03 | 897 | 1426 | 2868 | 4019 | -0.0055432 | -0.0048849 | -0.014772 | -0.0088779
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00445 | 0.00445 | 0.0025 | 0.0025 | 0.0025 | 0.59846 | 8.173 | 258.366 | 0.03 | 896 | 1424 | 2853 | 4007 | -0.0044444 | -0.0048917 | -0.015188 | -0.0089043
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00476 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.59987 | 8.1826 | 258.366 | 0.03 | 894 | 1422 | 2839 | 3996 | -0.0055617 | -0.0042017 | -0.01492 | -0.0086827
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00469 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00436 | 0.00436 | 0.0025 | 0.0025 | 0.0025 | 0.60137 | 8.1929 | 258.366 | 0.03 | 893 | 1420 | 2824 | 3984 | -0.0044593 | -0.0042076 | -0.015342 | -0.0087086
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00418 | 0.00418 | 0.0025 | 0.0025 | 0.0025 | 0.60737 | 7.8985 | 272.816 | 0.03 | 886 | 1554 | 3072 | 4044 | -0.0044944 | -0.031776 | -0.013171 | -0.0041862
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00445 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00414 | 0.00414 | 0.0025 | 0.0025 | 0.0025 | 0.60935 | 8.7442 | 272.816 | 0.03 | 777 | 1243 | 1922 | 3155 | -0.0051216 | -0.0040064 | -0.020886 | -0.010662
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0041 | 0.0041 | 0.0025 | 0.0025 | 0.0025 | 0.61148 | 8.7594 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133 | -0.003856 | -0.0048193 | -0.021178 | -0.010423
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00436 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00405 | 0.00405 | 0.0025 | 0.0025 | 0.0025 | 0.61382 | 8.7762 | 272.816 | 0.03 | 772 | 1236 | 1867 | 3110 | -0.006435 | -0.0056315 | -0.028616 | -0.014263
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00432 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.6164 | 8.7946 | 272.816 | 0.03 | 771 | 1234 | 1853 | 3099 | -0.0051613 | -0.0040355 | -0.022164 | -0.010852

## Rho_25%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | % Change from Default rho
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00524 | 0.00436 | 0.00881 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00817 | 0.00817 | 0.00313 | 0.00313 | 0.00313 | 0.3245 | 3.8048 | 186.116 | 0.03 | 3038 | 10996 | 11422 | 11865 | -0.10171 | -0.08443 | -0.081094 | -0.077587
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00519 | 0.00431 | 0.00873 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00809 | 0.00809 | 0.00313 | 0.00313 | 0.00313 | 0.33751 | 4.2888 | 186.116 | 0.03 | 2667 | 9854 | 10286 | 10737 | -0.10262 | -0.087255 | -0.083489 | -0.079712
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00513 | 0.00428 | 0.00863 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00801 | 0.00801 | 0.00313 | 0.00313 | 0.00313 | 0.35184 | 4.3789 | 186.116 | 0.03 | 2607 | 9665 | 10098 | 10550 | -0.096047 | -0.082059 | -0.078481 | -0.074886
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.00423 | 0.00852 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00794 | 0.00794 | 0.00313 | 0.00313 | 0.00313 | 0.3692 | 4.4856 | 186.116 | 0.03 | 2537 | 9442 | 9875 | 10329 | -0.091983 | -0.078919 | -0.075461 | -0.071884
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00501 | 0.00419 | 0.00844 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00785 | 0.00785 | 0.00313 | 0.00313 | 0.00313 | 0.39197 | 4.6218 | 186.116 | 0.03 | 2459 | 9188 | 9622 | 10077 | -0.085193 | -0.073697 | -0.070338 | -0.067031
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00459 | 0.00313 | 0.00774 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00719 | 0.00719 | 0.00313 | 0.00313 | 0.00313 | 0.51558 | 5.2093 | 200.566 | 0.03 | 1993 | 7567 | 7971 | 8398 | -0.043207 | -0.038745 | -0.036854 | -0.034934
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00455 | 0.00313 | 0.00766 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00711 | 0.00711 | 0.00313 | 0.00313 | 0.00313 | 0.51838 | 5.7733 | 200.566 | 0.03 | 1771 | 6798 | 7202 | 7630 | -0.044253 | -0.040644 | -0.038451 | -0.036373
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0045 | 0.00313 | 0.00758 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00702 | 0.00702 | 0.00313 | 0.00313 | 0.00313 | 0.52146 | 5.7904 | 200.566 | 0.03 | 1763 | 6773 | 7177 | 7605 | -0.044444 | -0.040516 | -0.038451 | -0.036244
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00445 | 0.00313 | 0.0075 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00698 | 0.00698 | 0.00313 | 0.00313 | 0.00313 | 0.52489 | 5.8094 | 200.566 | 0.03 | 1756 | 6748 | 7152 | 7579 | -0.044094 | -0.040387 | -0.038322 | -0.036241
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0044 | 0.00313 | 0.00741 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00689 | 0.00689 | 0.00313 | 0.00313 | 0.00313 | 0.52916 | 5.8329 | 200.566 | 0.03 | 1749 | 6723 | 7127 | 7554 | -0.044262 | -0.040394 | -0.038192 | -0.036234
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00407 | 0.00313 | 0.00687 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00638 | 0.00638 | 0.00313 | 0.00313 | 0.00313 | 0.57102 | 5.9173 | 215.016 | 0.03 | 1603 | 6169 | 6545 | 6944 | -0.037237 | -0.034736 | -0.032949 | -0.031115
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00405 | 0.00313 | 0.0068 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00631 | 0.00631 | 0.00313 | 0.00313 | 0.00313 | 0.58583 | 6.6245 | 215.016 | 0.03 | 1402 | 4739 | 5812 | 6209 | -0.034435 | -0.079806 | -0.031172 | -0.029389
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.004 | 0.00313 | 0.00674 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00625 | 0.00625 | 0.00313 | 0.00313 | 0.00313 | 0.60404 | 6.7266 | 215.016 | 0.03 | 1374 | 4501 | 5707 | 6104 | -0.030346 | -0.07558 | -0.027768 | -0.026165
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00395 | 0.00313 | 0.00665 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00619 | 0.00619 | 0.00313 | 0.00313 | 0.00313 | 0.60374 | 6.725 | 215.016 | 0.03 | 1376 | 4523 | 5717 | 6114 | -0.028934 | -0.071062 | -0.026065 | -0.024569
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00313 | 0.0066 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00613 | 0.00613 | 0.00313 | 0.00313 | 0.00313 | 0.60394 | 6.7261 | 215.016 | 0.03 | 1374 | 4501 | 5707 | 6104 | -0.032394 | -0.07955 | -0.029422 | -0.027716
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00617 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00574 | 0.00574 | 0.00313 | 0.00313 | 0.00313 | 0.59564 | 6.488 | 229.466 | 0.03 | 1345 | 4703 | 5563 | 5936 | -0.020393 | -0.04527 | -0.018352 | -0.017219
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00611 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00567 | 0.00567 | 0.00313 | 0.00313 | 0.00313 | 0.59622 | 7.1745 | 229.466 | 0.03 | 1190 | 3326 | 4840 | 5349 | -0.018961 | -0.062835 | -0.035664 | -0.016366
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00605 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00561 | 0.00561 | 0.00313 | 0.00313 | 0.00313 | 0.59684 | 7.1782 | 229.466 | 0.03 | 1188 | 3306 | 4824 | 5341 | -0.02061 | -0.06847 | -0.038852 | -0.017837
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00599 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00555 | 0.00555 | 0.00313 | 0.00313 | 0.00313 | 0.59749 | 7.1821 | 229.466 | 0.03 | 1188 | 3306 | 4824 | 5341 | -0.018993 | -0.062925 | -0.035779 | -0.01639
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00593 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.0055 | 0.0055 | 0.00313 | 0.00313 | 0.00313 | 0.5982 | 7.1864 | 229.466 | 0.03 | 1186 | 3285 | 4808 | 5333 | -0.020644 | -0.068878 | -0.038977 | -0.017864
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00559 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00519 | 0.00519 | 0.00313 | 0.00313 | 0.00313 | 0.60262 | 6.9731 | 243.916 | 0.03 | 1160 | 3510 | 4838 | 5187 | -0.019442 | -0.056452 | -0.017665 | -0.016682
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00554 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00514 | 0.00514 | 0.00313 | 0.00313 | 0.00313 | 0.60354 | 7.713 | 243.916 | 0.03 | 1022 | 2100 | 3727 | 4648 | -0.020134 | -0.097938 | -0.047047 | -0.017336
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00548 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00508 | 0.00508 | 0.00313 | 0.00313 | 0.00313 | 0.60449 | 7.719 | 243.916 | 0.03 | 1021 | 2081 | 3712 | 4642 | -0.021093 | -0.1061 | -0.050882 | -0.018605
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00543 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00503 | 0.00503 | 0.00313 | 0.00313 | 0.00313 | 0.60551 | 7.7256 | 243.916 | 0.03 | 1019 | 2062 | 3696 | 4635 | -0.021134 | -0.10697 | -0.051091 | -0.018632
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00536 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00499 | 0.00499 | 0.00313 | 0.00313 | 0.00313 | 0.60657 | 7.7323 | 243.916 | 0.03 | 1019 | 2062 | 3696 | 4635 | -0.021134 | -0.10697 | -0.051091 | -0.018632
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00511 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00474 | 0.00474 | 0.00313 | 0.00313 | 0.00313 | 0.61201 | 7.4779 | 258.366 | 0.03 | 1003 | 2396 | 3850 | 4537 | -0.021463 | -0.088973 | -0.046558 | -0.019027
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00505 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00469 | 0.00469 | 0.00313 | 0.00313 | 0.00313 | 0.61335 | 8.2741 | 258.366 | 0.03 | 882 | 1403 | 2709 | 3889 | -0.022173 | -0.020935 | -0.069392 | -0.040937
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.005 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00464 | 0.00464 | 0.00313 | 0.00313 | 0.00313 | 0.61481 | 8.2839 | 258.366 | 0.03 | 880 | 1401 | 2694 | 3877 | -0.022222 | -0.020964 | -0.070072 | -0.041059
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00495 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00459 | 0.00459 | 0.00313 | 0.00313 | 0.00313 | 0.61639 | 8.2946 | 258.366 | 0.03 | 879 | 1399 | 2680 | 3865 | -0.022247 | -0.020308 | -0.07009 | -0.041181
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00489 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00455 | 0.00455 | 0.00313 | 0.00313 | 0.00313 | 0.6181 | 8.3061 | 258.366 | 0.03 | 876 | 1395 | 2651 | 3841 | -0.023411 | -0.021739 | -0.075662 | -0.04429
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00469 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00436 | 0.00436 | 0.00313 | 0.00313 | 0.00313 | 0.62488 | 8.0116 | 272.816 | 0.03 | 870 | 1381 | 2921 | 3975 | -0.022472 | -0.13956 | -0.061677 | -0.021177
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00464 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00431 | 0.00431 | 0.00313 | 0.00313 | 0.00313 | 0.62708 | 8.8704 | 272.816 | 0.03 | 762 | 1220 | 1744 | 3009 | -0.024328 | -0.022436 | -0.11156 | -0.056444
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00459 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00426 | 0.00426 | 0.00313 | 0.00313 | 0.00313 | 0.62943 | 8.887 | 272.816 | 0.03 | 760 | 1217 | 1717 | 2987 | -0.023136 | -0.02249 | -0.11312 | -0.056538
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.00455 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00423 | 0.00423 | 0.00313 | 0.00313 | 0.00313 | 0.63204 | 8.9055 | 272.816 | 0.03 | 758 | 1214 | 1689 | 2964 | -0.024453 | -0.023331 | -0.12123 | -0.060539
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.00313 | 0.0045 | 0.00313 | 0.00313 | 0.00313 | 0.00313 | 0.00417 | 0.00417 | 0.00313 | 0.00313 | 0.00313 | 0.63486 | 8.9253 | 272.816 | 0.03 | 755 | 1210 | 1662 | 2942 | -0.025806 | -0.023406 | -0.12296 | -0.060964

## Rho_50%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | % Change from Default rho
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00418 | 0.00846 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00785 | 0.00785 | 0.00375 | 0.00375 | 0.00375 | 0.3424 | 3.9084 | 186.116 | 0.03 | 2947 | 10722 | 11149 | 11594 | -0.12862 | -0.10724 | -0.10306 | -0.098655
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00414 | 0.00837 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00777 | 0.00777 | 0.00375 | 0.00375 | 0.00375 | 0.3554 | 4.401 | 186.116 | 0.03 | 2594 | 9624 | 10057 | 10509 | -0.12719 | -0.10856 | -0.10389 | -0.099254
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00411 | 0.00828 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0077 | 0.0077 | 0.00375 | 0.00375 | 0.00375 | 0.36956 | 4.4878 | 186.116 | 0.03 | 2537 | 9442 | 9875 | 10329 | -0.12032 | -0.10324 | -0.098832 | -0.094265
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00819 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00762 | 0.00762 | 0.00375 | 0.00375 | 0.00375 | 0.38641 | 4.589 | 186.116 | 0.03 | 2477 | 9245 | 9680 | 10134 | -0.11346 | -0.098137 | -0.093718 | -0.089406
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00481 | 0.00402 | 0.0081 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00753 | 0.00753 | 0.00375 | 0.00375 | 0.00375 | 0.40802 | 4.7156 | 186.116 | 0.03 | 2401 | 8999 | 9434 | 9890 | -0.10677 | -0.092751 | -0.088502 | -0.084344
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.00375 | 0.00743 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0069 | 0.0069 | 0.00375 | 0.00375 | 0.00375 | 0.52134 | 5.2383 | 200.566 | 0.03 | 1980 | 7522 | 7927 | 8353 | -0.049448 | -0.044461 | -0.04217 | -0.040106
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00436 | 0.00375 | 0.00735 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00683 | 0.00683 | 0.00375 | 0.00375 | 0.00375 | 0.52412 | 5.8051 | 200.566 | 0.03 | 1756 | 6748 | 7152 | 7579 | -0.052348 | -0.0477 | -0.045127 | -0.042814
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.00375 | 0.00728 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00675 | 0.00675 | 0.00375 | 0.00375 | 0.00375 | 0.52734 | 5.823 | 200.566 | 0.03 | 1753 | 6735 | 7139 | 7567 | -0.049864 | -0.045899 | -0.043542 | -0.041059
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00428 | 0.00375 | 0.0072 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00669 | 0.00669 | 0.00375 | 0.00375 | 0.00375 | 0.53085 | 5.8423 | 200.566 | 0.03 | 1746 | 6710 | 7114 | 7542 | -0.049537 | -0.045791 | -0.043431 | -0.040946
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00423 | 0.00375 | 0.00711 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00661 | 0.00661 | 0.00375 | 0.00375 | 0.00375 | 0.53518 | 5.8661 | 200.566 | 0.03 | 1735 | 6673 | 7077 | 7505 | -0.051913 | -0.047531 | -0.044939 | -0.042485
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00375 | 0.0066 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00612 | 0.00612 | 0.00375 | 0.00375 | 0.00375 | 0.57484 | 5.9371 | 215.016 | 0.03 | 1596 | 6146 | 6522 | 6922 | -0.041441 | -0.038335 | -0.036348 | -0.034184
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00388 | 0.00375 | 0.00652 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00606 | 0.00606 | 0.00375 | 0.00375 | 0.00375 | 0.58782 | 6.6358 | 215.016 | 0.03 | 1397 | 4696 | 5792 | 6190 | -0.037879 | -0.088155 | -0.034506 | -0.032359
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00384 | 0.00375 | 0.00647 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.006 | 0.006 | 0.00375 | 0.00375 | 0.00375 | 0.60333 | 6.7227 | 215.016 | 0.03 | 1376 | 4523 | 5717 | 6114 | -0.028934 | -0.071062 | -0.026065 | -0.024569
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0038 | 0.00375 | 0.00639 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00594 | 0.00594 | 0.00375 | 0.00375 | 0.00375 | 0.60313 | 6.7216 | 215.016 | 0.03 | 1376 | 4523 | 5717 | 6114 | -0.028934 | -0.071062 | -0.026065 | -0.024569
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00377 | 0.00375 | 0.00633 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00588 | 0.00588 | 0.00375 | 0.00375 | 0.00375 | 0.60324 | 6.7222 | 215.016 | 0.03 | 1376 | 4523 | 5717 | 6114 | -0.030986 | -0.075051 | -0.027721 | -0.026123
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00593 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0055 | 0.0055 | 0.00375 | 0.00375 | 0.00375 | 0.60734 | 6.5515 | 229.466 | 0.03 | 1330 | 4581 | 5508 | 5881 | -0.031318 | -0.070037 | -0.028057 | -0.026325
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00587 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00545 | 0.00545 | 0.00375 | 0.00375 | 0.00375 | 0.60801 | 7.2451 | 229.466 | 0.03 | 1174 | 3164 | 4710 | 5285 | -0.032152 | -0.10848 | -0.061566 | -0.028135
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00581 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00539 | 0.00539 | 0.00375 | 0.00375 | 0.00375 | 0.60872 | 7.2493 | 229.466 | 0.03 | 1174 | 3164 | 4710 | 5285 | -0.032152 | -0.10848 | -0.061566 | -0.028135
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00575 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00533 | 0.00533 | 0.00375 | 0.00375 | 0.00375 | 0.60946 | 7.2537 | 229.466 | 0.03 | 1174 | 3164 | 4710 | 5285 | -0.030553 | -0.10317 | -0.058565 | -0.026703
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00568 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00528 | 0.00528 | 0.00375 | 0.00375 | 0.00375 | 0.61027 | 7.2585 | 229.466 | 0.03 | 1172 | 3144 | 4694 | 5277 | -0.032205 | -0.10884 | -0.061763 | -0.028177
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00537 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00498 | 0.00498 | 0.00375 | 0.00375 | 0.00375 | 0.6153 | 7.0461 | 243.916 | 0.03 | 1144 | 3358 | 4737 | 5125 | -0.032967 | -0.097312 | -0.038173 | -0.028436
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00531 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00493 | 0.00493 | 0.00375 | 0.00375 | 0.00375 | 0.6163 | 7.7941 | 243.916 | 0.03 | 1009 | 1947 | 3605 | 4595 | -0.032598 | -0.16366 | -0.078241 | -0.028541
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00525 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00487 | 0.00487 | 0.00375 | 0.00375 | 0.00375 | 0.61736 | 7.8008 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588 | -0.034516 | -0.17182 | -0.082332 | -0.030021
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0052 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00483 | 0.00483 | 0.00375 | 0.00375 | 0.00375 | 0.61851 | 7.8081 | 243.916 | 0.03 | 1006 | 1909 | 3574 | 4582 | -0.033622 | -0.17324 | -0.082413 | -0.029854
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00514 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00479 | 0.00479 | 0.00375 | 0.00375 | 0.00375 | 0.6197 | 7.8156 | 243.916 | 0.03 | 1004 | 1890 | 3559 | 4575 | -0.035543 | -0.18146 | -0.086264 | -0.031336
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0049 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00455 | 0.00455 | 0.00375 | 0.00375 | 0.00375 | 0.62575 | 7.5614 | 258.366 | 0.03 | 989 | 2252 | 3735 | 4484 | -0.035122 | -0.14373 | -0.075037 | -0.030486
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00484 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0045 | 0.0045 | 0.00375 | 0.00375 | 0.00375 | 0.62723 | 8.3672 | 258.366 | 0.03 | 868 | 1383 | 2564 | 3770 | -0.037694 | -0.034892 | -0.1192 | -0.070284
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0048 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00445 | 0.00445 | 0.00375 | 0.00375 | 0.00375 | 0.62884 | 8.3779 | 258.366 | 0.03 | 867 | 1381 | 2550 | 3758 | -0.036667 | -0.034941 | -0.11978 | -0.070492
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00476 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00441 | 0.00441 | 0.00375 | 0.00375 | 0.00375 | 0.63059 | 8.3896 | 258.366 | 0.03 | 865 | 1379 | 2535 | 3746 | -0.03782 | -0.034314 | -0.1204 | -0.070702
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00469 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00436 | 0.00436 | 0.00375 | 0.00375 | 0.00375 | 0.63246 | 8.402 | 258.366 | 0.03 | 864 | 1377 | 2521 | 3735 | -0.036789 | -0.034362 | -0.12099 | -0.070664
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0045 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00418 | 0.00418 | 0.00375 | 0.00375 | 0.00375 | 0.63986 | 8.107 | 272.816 | 0.03 | 857 | 1361 | 2784 | 3862 | -0.037079 | -0.15202 | -0.10569 | -0.049003
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00445 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00414 | 0.00414 | 0.00375 | 0.00375 | 0.00375 | 0.64224 | 8.977 | 272.816 | 0.03 | 750 | 1202 | 1593 | 2885 | -0.039693 | -0.036859 | -0.18849 | -0.095328
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00441 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0041 | 0.0041 | 0.00375 | 0.00375 | 0.00375 | 0.64478 | 8.9947 | 272.816 | 0.03 | 749 | 1200 | 1580 | 2874 | -0.037275 | -0.036145 | -0.18388 | -0.09223
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00436 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00405 | 0.00405 | 0.00375 | 0.00375 | 0.00375 | 0.64754 | 9.014 | 272.816 | 0.03 | 746 | 1197 | 1564 | 2852 | -0.039897 | -0.037007 | -0.18626 | -0.096038
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00432 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004 | 0.004 | 0.00375 | 0.00375 | 0.00375 | 0.65056 | 9.035 | 272.816 | 0.03 | 744 | 1194 | 1560 | 2829 | -0.04 | -0.03632 | -0.17678 | -0.097032

## Rho_100%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | % Change from Default rho
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0067 | 0.00558 | 0.01128 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01046 | 0.01046 | 0.005 | 0.005 | 0.005 | 0.40562 | 4.2539 | 186.116 | 0.03 | 2695 | 9940 | 10372 | 10822 | -0.20313 | -0.17236 | -0.16557 | -0.15867
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00664 | 0.00552 | 0.01116 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01036 | 0.01036 | 0.005 | 0.005 | 0.005 | 0.41801 | 4.7729 | 186.116 | 0.03 | 2373 | 8907 | 9343 | 9799 | -0.20155 | -0.17497 | -0.16751 | -0.16011
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00656 | 0.00548 | 0.01104 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01026 | 0.01026 | 0.005 | 0.005 | 0.005 | 0.4312 | 4.8476 | 186.116 | 0.03 | 2329 | 8763 | 9199 | 9656 | -0.19244 | -0.16773 | -0.16052 | -0.15328
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0065 | 0.0054 | 0.01092 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01016 | 0.01016 | 0.005 | 0.005 | 0.005 | 0.44658 | 4.9333 | 186.116 | 0.03 | 2287 | 8623 | 9058 | 9516 | -0.18146 | -0.15881 | -0.15195 | -0.14494
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00642 | 0.00536 | 0.0108 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01004 | 0.01004 | 0.005 | 0.005 | 0.005 | 0.46575 | 5.0381 | 186.116 | 0.03 | 2230 | 8435 | 8871 | 9329 | -0.17039 | -0.14961 | -0.1429 | -0.13628
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00588 | 0.005 | 0.0099 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0092 | 0.0092 | 0.005 | 0.005 | 0.005 | 0.5596 | 5.4271 | 200.566 | 0.03 | 1900 | 7250 | 7655 | 8082 | -0.087854 | -0.079014 | -0.075036 | -0.071248
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00582 | 0.005 | 0.0098 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0091 | 0.0091 | 0.005 | 0.005 | 0.005 | 0.56232 | 6.013 | 200.566 | 0.03 | 1687 | 6492 | 6906 | 7334 | -0.089584 | -0.083827 | -0.077971 | -0.073756
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00576 | 0.005 | 0.0097 | 0.005 | 0.005 | 0.005 | 0.005 | 0.009 | 0.009 | 0.005 | 0.005 | 0.005 | 0.56545 | 6.0297 | 200.566 | 0.03 | 1681 | 6446 | 6882 | 7310 | -0.088889 | -0.086839 | -0.077974 | -0.073628
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0057 | 0.005 | 0.0096 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00892 | 0.00892 | 0.005 | 0.005 | 0.005 | 0.5688 | 6.0475 | 200.566 | 0.03 | 1674 | 6399 | 6859 | 7286 | -0.088732 | -0.090017 | -0.07772 | -0.073499
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00564 | 0.005 | 0.00948 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00882 | 0.00882 | 0.005 | 0.005 | 0.005 | 0.57289 | 6.0692 | 200.566 | 0.03 | 1668 | 6353 | 6835 | 7263 | -0.088525 | -0.093206 | -0.077598 | -0.073361
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00522 | 0.005 | 0.0088 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00816 | 0.00816 | 0.005 | 0.005 | 0.005 | 0.60789 | 6.1054 | 215.016 | 0.03 | 1544 | 5841 | 6333 | 6732 | -0.072673 | -0.086059 | -0.064273 | -0.060695
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00518 | 0.005 | 0.0087 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00808 | 0.00808 | 0.005 | 0.005 | 0.005 | 0.6183 | 6.8056 | 215.016 | 0.03 | 1354 | 4328 | 5633 | 6030 | -0.067493 | -0.15961 | -0.06101 | -0.057371
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00512 | 0.005 | 0.00862 | 0.005 | 0.005 | 0.005 | 0.005 | 0.008 | 0.008 | 0.005 | 0.005 | 0.005 | 0.63005 | 6.87 | 215.016 | 0.03 | 1340 | 4198 | 5578 | 5975 | -0.05434 | -0.13781 | -0.049744 | -0.046745
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00506 | 0.005 | 0.00852 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00792 | 0.00792 | 0.005 | 0.005 | 0.005 | 0.62978 | 6.8685 | 215.016 | 0.03 | 1340 | 4198 | 5578 | 5975 | -0.05434 | -0.13781 | -0.049744 | -0.046745
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00502 | 0.005 | 0.00844 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00784 | 0.00784 | 0.005 | 0.005 | 0.005 | 0.62988 | 6.869 | 215.016 | 0.03 | 1340 | 4198 | 5578 | 5975 | -0.056338 | -0.14151 | -0.051361 | -0.048264
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.0079 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00734 | 0.00734 | 0.005 | 0.005 | 0.005 | 0.63476 | 6.6977 | 229.466 | 0.03 | 1294 | 4278 | 5373 | 5745 | -0.057538 | -0.13155 | -0.051879 | -0.048841
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00782 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00726 | 0.00726 | 0.005 | 0.005 | 0.005 | 0.63554 | 7.4073 | 229.466 | 0.03 | 1142 | 2840 | 4450 | 5161 | -0.058533 | -0.19977 | -0.11337 | -0.050938
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00774 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00718 | 0.00718 | 0.005 | 0.005 | 0.005 | 0.63635 | 7.412 | 229.466 | 0.03 | 1142 | 2840 | 4450 | 5161 | -0.058533 | -0.19977 | -0.11337 | -0.050938
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00766 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0071 | 0.0071 | 0.005 | 0.005 | 0.005 | 0.6372 | 7.417 | 229.466 | 0.03 | 1140 | 2820 | 4433 | 5154 | -0.058629 | -0.20068 | -0.11393 | -0.050829
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00758 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00704 | 0.00704 | 0.005 | 0.005 | 0.005 | 0.63813 | 7.4224 | 229.466 | 0.03 | 1140 | 2820 | 4433 | 5154 | -0.058629 | -0.20068 | -0.11393 | -0.050829
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00716 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00664 | 0.00664 | 0.005 | 0.005 | 0.005 | 0.64401 | 7.2086 | 243.916 | 0.03 | 1112 | 3053 | 4492 | 5003 | -0.060017 | -0.1793 | -0.087919 | -0.051564
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00708 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00658 | 0.00658 | 0.005 | 0.005 | 0.005 | 0.64515 | 7.9744 | 243.916 | 0.03 | 980 | 1604 | 3329 | 4478 | -0.060403 | -0.311 | -0.14881 | -0.053277
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.007 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0065 | 0.0065 | 0.005 | 0.005 | 0.005 | 0.64635 | 7.9819 | 243.916 | 0.03 | 978 | 1585 | 3314 | 4471 | -0.06232 | -0.31916 | -0.15265 | -0.054757
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00694 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00644 | 0.00644 | 0.005 | 0.005 | 0.005 | 0.64766 | 7.9899 | 243.916 | 0.03 | 977 | 1566 | 3298 | 4465 | -0.061479 | -0.32178 | -0.15327 | -0.054626
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00686 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00638 | 0.00638 | 0.005 | 0.005 | 0.005 | 0.649 | 7.9982 | 243.916 | 0.03 | 975 | 1547 | 3283 | 4459 | -0.063401 | -0.33001 | -0.15712 | -0.055897
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00654 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00606 | 0.00606 | 0.005 | 0.005 | 0.005 | 0.65593 | 7.7416 | 258.366 | 0.03 | 960 | 1929 | 3475 | 4369 | -0.063415 | -0.26654 | -0.13943 | -0.055351
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00646 | 0.005 | 0.005 | 0.005 | 0.005 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.65759 | 8.5673 | 258.366 | 0.03 | 842 | 1344 | 2275 | 3533 | -0.066519 | -0.062107 | -0.21848 | -0.12873
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.0064 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00594 | 0.00594 | 0.005 | 0.005 | 0.005 | 0.65938 | 8.5789 | 258.366 | 0.03 | 841 | 1342 | 2261 | 3521 | -0.065556 | -0.062194 | -0.21954 | -0.12911
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00634 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00588 | 0.00588 | 0.005 | 0.005 | 0.005 | 0.66132 | 8.5916 | 258.366 | 0.03 | 839 | 1340 | 2246 | 3509 | -0.066741 | -0.061625 | -0.22068 | -0.1295
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00626 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00582 | 0.00582 | 0.005 | 0.005 | 0.005 | 0.66339 | 8.605 | 258.366 | 0.03 | 838 | 1338 | 2232 | 3497 | -0.065775 | -0.061711 | -0.22176 | -0.12988
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.006 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00558 | 0.00558 | 0.005 | 0.005 | 0.005 | 0.67161 | 8.3057 | 272.816 | 0.03 | 830 | 1322 | 2511 | 3638 | -0.067416 | -0.17632 | -0.19338 | -0.10416
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00594 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00552 | 0.00552 | 0.005 | 0.005 | 0.005 | 0.67419 | 9.1976 | 272.816 | 0.03 | 726 | 1166 | 1526 | 2638 | -0.070423 | -0.065705 | -0.22262 | -0.17278
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00588 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00546 | 0.00546 | 0.005 | 0.005 | 0.005 | 0.67694 | 9.2163 | 272.816 | 0.03 | 724 | 1163 | 1522 | 2616 | -0.069409 | -0.065863 | -0.21384 | -0.17372
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00582 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0054 | 0.0054 | 0.005 | 0.005 | 0.005 | 0.6799 | 9.2365 | 272.816 | 0.03 | 722 | 1160 | 1518 | 2593 | -0.070785 | -0.066774 | -0.2102 | -0.17813
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00576 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00534 | 0.00534 | 0.005 | 0.005 | 0.005 | 0.68312 | 9.2583 | 272.816 | 0.03 | 720 | 1157 | 1514 | 2571 | -0.070968 | -0.066182 | -0.20106 | -0.17938

## damping_study
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.02 | 3664 | 18016 | 18644 | 19295
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.025 | 3519 | 14413 | 14916 | 15436
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.03 | 3382 | 12010 | 12430 | 12863
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.035 | 3253 | 10295 | 10654 | 11026
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.04 | 3130 | 9008 | 9322 | 9647
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.045 | 3014 | 8007 | 8286 | 8576
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26407 | 3.4323 | 186.116 | 0.05 | 2903 | 7206 | 7458 | 7718
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.02 | 3242 | 16156 | 16797 | 17464
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.025 | 3099 | 12925 | 13438 | 13971
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.03 | 2964 | 10771 | 11198 | 11642
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.035 | 2837 | 9232 | 9598 | 9979
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.04 | 2718 | 8078 | 8399 | 8732
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.045 | 2605 | 7181 | 7465 | 7762
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.27701 | 3.8854 | 186.116 | 0.05 | 2500 | 6463 | 6719 | 6985
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.02 | 3162 | 15794 | 16437 | 17106
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.025 | 3019 | 12635 | 13150 | 13685
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.03 | 2884 | 10529 | 10958 | 11404
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.035 | 2758 | 9025 | 9393 | 9775
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.04 | 2640 | 7897 | 8218 | 8553
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.045 | 2528 | 7020 | 7305 | 7603
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29155 | 3.9861 | 186.116 | 0.05 | 2424 | 6318 | 6575 | 6842
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.02 | 3071 | 15376 | 16021 | 16693
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.025 | 2928 | 12301 | 12817 | 13355
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.03 | 2794 | 10251 | 10681 | 11129
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.035 | 2669 | 8786 | 9155 | 9539
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.04 | 2551 | 7688 | 8011 | 8347
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.045 | 2441 | 6834 | 7121 | 7419
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.30937 | 4.1061 | 186.116 | 0.05 | 2337 | 6150 | 6408 | 6677
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.02 | 2963 | 14878 | 15526 | 16201
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.025 | 2821 | 11902 | 12420 | 12961
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.03 | 2688 | 9919 | 10350 | 10801
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.035 | 2563 | 8502 | 8872 | 9258
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.04 | 2447 | 7439 | 7763 | 8101
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.045 | 2338 | 6612 | 6900 | 7201
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33334 | 4.2622 | 186.116 | 0.05 | 2236 | 5951 | 6210 | 6481
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.02 | 2332 | 11808 | 12415 | 13052
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.025 | 2203 | 9446 | 9932 | 10442
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.03 | 2083 | 7872 | 8276 | 8702
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.035 | 1973 | 6747 | 7094 | 7459
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.04 | 1871 | 5904 | 6207 | 6526
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.045 | 1776 | 5248 | 5518 | 5801
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.0091 | 200.566 | 0.05 | 1688 | 4723 | 4966 | 5221
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.02 | 2096 | 10629 | 11236 | 11877
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.025 | 1969 | 8503 | 8989 | 9502
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.03 | 1853 | 7086 | 7490 | 7918
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.035 | 1746 | 6074 | 6420 | 6787
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.04 | 1648 | 5315 | 5618 | 5938
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.045 | 1558 | 4724 | 4994 | 5279
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47935 | 5.5517 | 200.566 | 0.05 | 1475 | 4252 | 4494 | 4751
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.02 | 2088 | 10589 | 11195 | 11837
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.025 | 1961 | 8471 | 8956 | 9469
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.03 | 1845 | 7059 | 7464 | 7891
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.035 | 1738 | 6051 | 6397 | 6764
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.04 | 1640 | 5294 | 5598 | 5918
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.045 | 1550 | 4706 | 4976 | 5261
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48246 | 5.5696 | 200.566 | 0.05 | 1468 | 4236 | 4478 | 4735
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.02 | 2080 | 10549 | 11155 | 11797
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.025 | 1953 | 8439 | 8924 | 9437
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.03 | 1837 | 7032 | 7437 | 7864
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.035 | 1731 | 6028 | 6374 | 6741
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.04 | 1633 | 5274 | 5578 | 5898
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.045 | 1543 | 4688 | 4958 | 5243
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48589 | 5.5894 | 200.566 | 0.05 | 1461 | 4219 | 4462 | 4719
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.02 | 2072 | 10509 | 11115 | 11757
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.025 | 1946 | 8407 | 8892 | 9405
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.03 | 1830 | 7006 | 7410 | 7838
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.035 | 1723 | 6005 | 6352 | 6718
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.04 | 1626 | 5254 | 5558 | 5878
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.045 | 1536 | 4671 | 4940 | 5225
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.49021 | 5.6142 | 200.566 | 0.05 | 1454 | 4204 | 4446 | 4703
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.02 | 1891 | 9586 | 10151 | 10750
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.025 | 1773 | 7669 | 8121 | 8600
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.03 | 1665 | 6391 | 6768 | 7167
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.035 | 1567 | 5478 | 5801 | 6143
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.04 | 1477 | 4793 | 5076 | 5375
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.045 | 1394 | 4260 | 4512 | 4778
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53451 | 5.725 | 215.016 | 0.05 | 1318 | 3834 | 4061 | 4300
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.02 | 1671 | 7590 | 8998 | 9595
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.025 | 1556 | 6130 | 7198 | 7676
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.03 | 1452 | 5150 | 5999 | 6397
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.035 | 1358 | 4443 | 5142 | 5483
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.04 | 1273 | 3911 | 4499 | 4798
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.045 | 1195 | 3494 | 3999 | 4265
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.55144 | 6.4271 | 215.016 | 0.05 | 1125 | 3157 | 3599 | 3838
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.02 | 1634 | 7129 | 8805 | 9402
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.025 | 1520 | 5778 | 7044 | 7521
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.03 | 1417 | 4869 | 5870 | 6268
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.035 | 1324 | 4212 | 5031 | 5372
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.045 | 1163 | 3324 | 3913 | 4178
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.5737 | 6.5555 | 215.016 | 0.05 | 1094 | 3009 | 3522 | 3761
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.02 | 1637 | 7164 | 8819 | 9416
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.025 | 1523 | 5805 | 7055 | 7533
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.03 | 1420 | 4890 | 5880 | 6278
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.035 | 1327 | 4229 | 5040 | 5381
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.04 | 1242 | 3730 | 4410 | 4708
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.045 | 1166 | 3337 | 3920 | 4185
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57357 | 6.5548 | 215.016 | 0.05 | 1096 | 3020 | 3528 | 3767
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.02 | 1634 | 7129 | 8805 | 9402
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.025 | 1520 | 5778 | 7044 | 7521
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.03 | 1417 | 4869 | 5870 | 6268
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.035 | 1324 | 4212 | 5031 | 5372
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.045 | 1163 | 3324 | 3913 | 4178
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.57366 | 6.5553 | 215.016 | 0.05 | 1094 | 3009 | 3522 | 3761
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.02 | 1578 | 7277 | 8500 | 9060
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.025 | 1471 | 5870 | 6800 | 7248
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.03 | 1373 | 4926 | 5667 | 6040
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.035 | 1285 | 4246 | 4857 | 5177
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.04 | 1205 | 3734 | 4250 | 4530
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.045 | 1132 | 3334 | 3778 | 4027
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57677 | 6.3844 | 229.466 | 0.05 | 1065 | 3011 | 3400 | 3624
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.02 | 1412 | 5014 | 7509 | 8157
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.025 | 1307 | 4144 | 6015 | 6526
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.03 | 1213 | 3549 | 5019 | 5438
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.035 | 1129 | 3110 | 4307 | 4661
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.04 | 1053 | 2774 | 3771 | 4079
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.045 | 985 | 2505 | 3355 | 3625
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57729 | 7.0597 | 229.466 | 0.05 | 923 | 2285 | 3022 | 3263
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.02 | 1412 | 5014 | 7509 | 8157
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.025 | 1307 | 4144 | 6015 | 6526
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.03 | 1213 | 3549 | 5019 | 5438
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.035 | 1129 | 3110 | 4307 | 4661
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.04 | 1053 | 2774 | 3771 | 4079
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.045 | 985 | 2505 | 3355 | 3625
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57784 | 7.063 | 229.466 | 0.05 | 923 | 2285 | 3022 | 3263
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.02 | 1410 | 4981 | 7481 | 8145
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.025 | 1305 | 4119 | 5995 | 6516
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.03 | 1211 | 3528 | 5003 | 5430
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.035 | 1127 | 3094 | 4294 | 4654
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.04 | 1051 | 2760 | 3760 | 4072
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.045 | 983 | 2493 | 3346 | 3620
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.57843 | 7.0666 | 229.466 | 0.05 | 921 | 2274 | 3014 | 3258
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.02 | 1410 | 4981 | 7481 | 8145
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.025 | 1305 | 4119 | 5995 | 6516
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.03 | 1211 | 3528 | 5003 | 5430
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.035 | 1127 | 3094 | 4294 | 4654
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.04 | 1051 | 2760 | 3760 | 4072
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.045 | 983 | 2493 | 3346 | 3620
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57906 | 7.0705 | 229.466 | 0.05 | 921 | 2274 | 3014 | 3258
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.02 | 1372 | 5344 | 7388 | 7912
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.025 | 1272 | 4377 | 5910 | 6330
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.03 | 1183 | 3720 | 4925 | 5275
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.035 | 1103 | 3242 | 4221 | 4521
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.04 | 1030 | 2876 | 3694 | 3956
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.045 | 964 | 2586 | 3283 | 3517
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58294 | 6.8583 | 243.916 | 0.05 | 905 | 2351 | 2955 | 3165
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.02 | 1225 | 3058 | 5682 | 7095
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.025 | 1129 | 2634 | 4625 | 5676
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58373 | 7.5853 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.02 | 1225 | 3058 | 5682 | 7095
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.025 | 1129 | 2634 | 4625 | 5676
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58457 | 7.5908 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.02 | 1223 | 3027 | 5656 | 7085
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.025 | 1127 | 2610 | 4605 | 5668
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.03 | 1041 | 2309 | 3895 | 4723
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.035 | 965 | 2079 | 3382 | 4049
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.04 | 896 | 1892 | 2991 | 3542
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.045 | 835 | 1738 | 2683 | 3149
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58549 | 7.5968 | 243.916 | 0.05 | 780 | 1607 | 2434 | 2834
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.02 | 1223 | 3027 | 5656 | 7085
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.025 | 1127 | 2610 | 4605 | 5668
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.03 | 1041 | 2309 | 3895 | 4723
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.035 | 965 | 2079 | 3382 | 4049
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.04 | 896 | 1892 | 2991 | 3542
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.045 | 835 | 1738 | 2683 | 3149
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58643 | 7.6029 | 243.916 | 0.05 | 780 | 1607 | 2434 | 2834
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.02 | 1199 | 3596 | 5954 | 6938
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.025 | 1107 | 3027 | 4808 | 5550
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.03 | 1025 | 2630 | 4038 | 4625
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.035 | 952 | 2332 | 3485 | 3964
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.04 | 886 | 2099 | 3067 | 3469
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.045 | 827 | 1911 | 2740 | 3083
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59121 | 7.3497 | 258.366 | 0.05 | 773 | 1754 | 2476 | 2775
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.02 | 1069 | 1646 | 4033 | 6039
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.025 | 980 | 1534 | 3370 | 4849
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.03 | 902 | 1433 | 2911 | 4055
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.035 | 832 | 1341 | 2571 | 3485
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.04 | 770 | 1257 | 2306 | 3056
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.045 | 715 | 1181 | 2094 | 2723
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59242 | 8.1317 | 258.366 | 0.05 | 666 | 1112 | 1917 | 2455
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.02 | 1067 | 1643 | 4008 | 6018
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.025 | 978 | 1532 | 3351 | 4834
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.03 | 900 | 1431 | 2897 | 4043
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.035 | 831 | 1339 | 2559 | 3475
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.04 | 769 | 1255 | 2296 | 3049
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.045 | 714 | 1179 | 2086 | 2717
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.59372 | 8.1406 | 258.366 | 0.05 | 665 | 1110 | 1910 | 2449
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.02 | 1066 | 1641 | 3984 | 5997
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.025 | 977 | 1530 | 3333 | 4818
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.03 | 899 | 1428 | 2882 | 4031
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.035 | 829 | 1337 | 2547 | 3466
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.04 | 768 | 1253 | 2287 | 3041
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.045 | 713 | 1177 | 2077 | 2710
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59516 | 8.1504 | 258.366 | 0.05 | 664 | 1108 | 1903 | 2444
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.02 | 1064 | 1639 | 3959 | 5976
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.025 | 976 | 1527 | 3315 | 4803
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.03 | 897 | 1426 | 2868 | 4019
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.035 | 828 | 1335 | 2535 | 3456
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.04 | 766 | 1251 | 2277 | 3033
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.045 | 712 | 1176 | 2069 | 2704
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59669 | 8.161 | 258.366 | 0.05 | 663 | 1106 | 1896 | 2439
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.02 | 1051 | 1950 | 4427 | 6092
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.025 | 966 | 1757 | 3646 | 4873
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.03 | 890 | 1605 | 3113 | 4061
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.035 | 823 | 1479 | 2724 | 3481
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.04 | 764 | 1371 | 2425 | 3046
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.045 | 710 | 1277 | 2187 | 2707
34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60274 | 7.8684 | 272.816 | 0.05 | 663 | 1194 | 1993 | 2437
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.02 | 934 | 1446 | 2467 | 4561
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.025 | 852 | 1342 | 2179 | 3745
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.03 | 781 | 1248 | 1963 | 3189
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.035 | 717 | 1164 | 1791 | 2784
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.04 | 662 | 1087 | 1649 | 2474
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.045 | 613 | 1019 | 1528 | 2229
34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60474 | 8.711 | 272.816 | 0.05 | 569 | 956 | 1423 | 2028
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.02 | 932 | 1442 | 2420 | 4521
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.025 | 850 | 1338 | 2144 | 3716
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.03 | 778 | 1245 | 1936 | 3166
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.035 | 715 | 1160 | 1769 | 2766
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.04 | 660 | 1084 | 1630 | 2460
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.045 | 610 | 1015 | 1512 | 2217
34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60689 | 8.7265 | 272.816 | 0.05 | 567 | 953 | 1409 | 2018
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.02 | 931 | 1440 | 2397 | 4501
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.025 | 849 | 1336 | 2127 | 3701
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.03 | 777 | 1243 | 1922 | 3155
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.035 | 714 | 1159 | 1758 | 2757
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.04 | 659 | 1082 | 1621 | 2452
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.045 | 609 | 1014 | 1504 | 2211
34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60925 | 8.7435 | 272.816 | 0.05 | 566 | 951 | 1402 | 2013
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.02 | 928 | 1436 | 2350 | 4462
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.025 | 846 | 1333 | 2092 | 3672
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.035 | 712 | 1155 | 1736 | 2739
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.04 | 656 | 1079 | 1603 | 2438
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.045 | 607 | 1011 | 1488 | 2199
34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61185 | 8.7621 | 272.816 | 0.05 | 564 | 948 | 1389 | 2003