## Slab_Properties
References:
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span |  |  |  | CRSI Design Guide for Vibration of Reinforced Concrete Floor Systems, First Edition
l2 = | 34 | ft | interior |  |  |  |  | ACI 318-14 Building Code Requirements for Structural Concrete
l1 / l2 = | 1 |  | * must be < 2.0, otherwise exhibits one way behavior |  |  |  |  | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
c1 = | 24 | in
c2 = | 24 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 12 | in
d = | 10.75 | in | *single layer of reinforcement
wc = | 150 | pcf
yt = | 6 | in
n = | 5.6374
lcw = | 1 |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = | 318.1981 | psi | * reduced modulus of rupture, per CRSI Design Guide p4-6
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 150 | psf
mass = | 5780 | lb sec2/ft
weight = | 186.116 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 308 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1340.416 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1340.416 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 697.0163 | k-ft
M1n1u = | 348.5082 | k-ft
M1n2u = | 938.2912 | k-ft
M2pu = | 469.1456 | k-ft
M2n1u = | 871.2704 | k-ft
M2n2u = | 871.2704 | k-ft
Service Moments
M01,DL = | 652.8 | k-ft | *includes SDL and self-weight
M01,LL = | 348.16 | k-ft
M02,DL = | 652.8 | k-ft
M02,LL = | 348.16 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 203.6736 | 135.7824 | k-ft
l1 | DL | n1 | 169.728 | 0 | k-ft
l1 | DL | n2 | 342.72 | 106.08 | k-ft
l1 | LL | p | 108.6259 | 72.4173 | k-ft
l1 | LL | n1 | 90.5216 | 0 | k-ft
l1 | LL | n2 | 182.784 | 60.928 | k-ft
l2 | DL | p | 137.088 | 91.392 | k-ft
l2 | DL | n1 | 318.24 | 106.08 | k-ft
l2 | DL | n2 | 318.24 | 106.08 | k-ft
l2 | LL | p | 73.1136 | 48.7424 | k-ft
l2 | LL | n1 | 169.728 | 56.576 | k-ft
l2 | LL | n2 | 169.728 | 56.576 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 418.2098 | 278.8065 | k-ft
l1 | n1 | 348.5082 | 0 | k-ft
l1 | n2 | 703.7184 | 224.7808 | k-ft
l2 | p | 281.4874 | 187.6582 | k-ft
l2 | n1 | 653.4528 | 217.8176 | k-ft
l2 | n2 | 653.4528 | 217.8176 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation (may be unconservative… ): | [6 empty] | User input (As from rho): |  |  |  |  | User input (rho):
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle
l1 | p | 7.3465 | 5.4825 | in2 | l1 | p | 7.3484 | 5.4825 | in2 | l1 | p | 7.3465 | 5.4825 |  | l1 | p | 0.00335 | 0.0025
l1 | n1 | 6.1185 | 5.4825 | in2 | l1 | n1 | 6.1237 | 5.4825 | in2 | l1 | n1 | 6.1185 | 5.4825 |  | l1 | n1 | 0.00279 | 0.0025
l1 | n2 | 12.3685 | 5.4825 | in2 | l1 | n2 | 12.3651 | 5.4825 | in2 | l1 | n2 | 12.3685 | 5.4825 |  | l1 | n2 | 0.00564 | 0.0025
l2 | p | 5.4825 | 5.4825 | in2 | l2 | p | 5.4825 | 5.4825 | in2 | l2 | p | 5.4825 | 5.4825 |  | l2 | p | 0.0025 | 0.0025
l2 | n1 | 11.4694 | 5.4825 | in2 | l2 | n1 | 11.4819 | 5.4825 | in2 | l2 | n1 | 11.4694 | 5.4825 |  | l2 | n1 | 0.00523 | 0.0025
l2 | n2 | 11.4694 | 5.4825 | in2 | l2 | n2 | 11.4819 | 5.4825 | in2 | l2 | n2 | 11.4694 | 5.4825 |  | l2 | n2 | 0.00523 | 0.0025
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 29376 | 29376 | in3
l1 | n1 | 29376 | 29376 | in3
l1 | n2 | 29376 | 29376 | in3
l2 | p | 29376 | 29376 | in3
l2 | n1 | 29376 | 29376 | in3
l2 | n2 | 29376 | 29376 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 4369.9861 | 4413.6222 | in3 | 4.9257 | 6.6004 | 1.8961 | 1.6597 | 3710.1817 | 2864.8547 | 129.8248 | 129.8248 | 0.41571 | 0.62356 | 0.0402 | 0.03
l1 | n1 | 4060.0209 | 29376 | in3 | 5.9143 | 6.6004 | 1.745 | 1.6597 | 3158.3144 | 2864.8547 | 129.8248 | 129.8248 | 0.49885 | 1.1 | 0.03348 | 0.03
l1 | n2 | 6100.2845 | 6301.2541 | in3 | 2.9257 | 6.6004 | 2.3905 | 1.6597 | 5801.4964 | 2864.8547 | 129.8248 | 129.8248 | 0.24705 | 0.77736 | 0.06768 | 0.03
l2 | p | 4368.849 | 12708.5009 | in3 | 6.6004 | 6.6004 | 1.6597 | 1.6597 | 2864.8547 | 2864.8547 | 129.8248 | 129.8248 | 0.61762 | 0.92643 | 0.03 | 0.03
l2 | n1 | 5777.1463 | 6739.6414 | in3 | 3.1551 | 6.6004 | 2.3127 | 1.6597 | 5444.002 | 2864.8547 | 129.8248 | 129.8248 | 0.26605 | 0.79816 | 0.06276 | 0.03
l2 | n2 | 5777.1463 | 6739.6414 | in3 | 3.1551 | 6.6004 | 2.3127 | 1.6597 | 5444.002 | 2864.8547 | 129.8248 | 129.8248 | 0.26605 | 0.79816 | 0.06276 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 4583.0361 | 8441.1237 | in3
l2 | 4791.3382 | 10917.8431 | in3
Calculate Panel Ie
Iep = | 15500.8791 | in3
Calculate Panel Ig
Igp = | 58752 | in3
Calculate k1
k1 = | 0.26384
Calculate fi |  |  | Interp li2
k2 = | 1.9 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 5 | slug / ft2 | 2 | 9.29
fi = | 3.4308 | Hz
Calculate/Input Parameters for DG11
W = | 186116 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits | [7 empty] | References:
fn= | 3.4308 | Hz | [5 empty] | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
W = | 186116 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips | Velocity
Very Slow | 3.4308 | 1.25 | - | - | - | - | - | 3128.9122 | - | 3128.9122 | - | 3128.9122 | mips
Slow | 3.4308 | 1.6 | 6.8 | 6 | 8 | 0.1 | 9005.3869 | 4765.8009 | 5266.7419 | 1782.7442 | N/A | 9005.3869 | mips | * does not consider mode scaling
Moderate | 3.4308 | 1.85 | 8 | 7 | 9 | 0.09 | 9319.7017 | 6064.4971 | 4731.9463 | 2024.0439 | N/A | 9319.7017 | mips
Fast | 3.4308 | 2.1 | 8.8 | 8 | 10 | 0.08 | 9644.9869 | 7459.0574 | 4382.2877 | 2253.4337 | N/A | 9644.9869 | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194

## thickness_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11

## thickness_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.025 | 4803 | 19209 | 19790 | 20388
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.03 | 4638 | 16007 | 16492 | 16990
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.035 | 4481 | 13721 | 14136 | 14563
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.04 | 4331 | 12006 | 12369 | 12743
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.045 | 4189 | 10672 | 10994 | 11327
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.05 | 4053 | 9604 | 9895 | 10194
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.055 | 3923 | 8731 | 8995 | 9267
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.06 | 3799 | 8004 | 8246 | 8495
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.065 | 3680 | 7388 | 7611 | 7842
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00622 | 0.00514 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.26483 | 2.9821 | 156.672 | 0.07 | 3567 | 6860 | 7068 | 7282
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.025 | 4324 | 17546 | 18124 | 18721
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.03 | 4164 | 14622 | 15103 | 15601
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.035 | 4013 | 12533 | 12946 | 13372
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.04 | 3868 | 10966 | 11327 | 11700
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.045 | 3731 | 9748 | 10069 | 10400
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.05 | 3601 | 8773 | 9062 | 9360
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.055 | 3477 | 7976 | 8238 | 8509
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.06 | 3360 | 7311 | 7552 | 7800
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.065 | 3248 | 6749 | 6971 | 7200
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00492 | 0.01034 | 0.00391 | 0.00205 | 0.00327 | 0.00343 | 0.00826 | 0.00826 | 0.00205 | 0.00211 | 0.00211 | 0.29786 | 3.2448 | 160.272 | 0.07 | 3141 | 6266 | 6473 | 6686
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.025 | 3643 | 15123 | 15702 | 16304
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.03 | 3489 | 12602 | 13085 | 13587
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.035 | 3344 | 10802 | 11216 | 11646
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.04 | 3207 | 9452 | 9814 | 10190
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.045 | 3078 | 8402 | 8723 | 9058
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.05 | 2957 | 7561 | 7851 | 8152
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.055 | 2842 | 6874 | 7137 | 7411
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.06 | 2734 | 6301 | 6543 | 6793
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.065 | 2631 | 5816 | 6039 | 6271
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00314 | 0.00329 | 0.0079 | 0.0079 | 0.00205 | 0.00205 | 0.00205 | 0.37997 | 3.7578 | 163.872 | 0.07 | 2535 | 5401 | 5608 | 5823
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.025 | 3425 | 14295 | 14865 | 15458
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.03 | 3275 | 11913 | 12388 | 12881
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.035 | 3134 | 10211 | 10618 | 11041
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.04 | 3002 | 8934 | 9291 | 9661
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.045 | 2877 | 7942 | 8258 | 8588
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.05 | 2760 | 7148 | 7433 | 7729
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.055 | 2649 | 6498 | 6757 | 7026
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.06 | 2545 | 5956 | 6194 | 6441
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.065 | 2447 | 5498 | 5717 | 5945
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00452 | 0.00946 | 0.00359 | 0.00204 | 0.00301 | 0.00316 | 0.00757 | 0.00757 | 0.00204 | 0.00204 | 0.00204 | 0.39237 | 3.9131 | 167.472 | 0.07 | 2355 | 5105 | 5309 | 5521
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.025 | 3250 | 13620 | 14180 | 14763
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.03 | 3104 | 11350 | 11817 | 12303
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.035 | 2967 | 9729 | 10129 | 10545
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.04 | 2838 | 8512 | 8863 | 9227
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.045 | 2718 | 7567 | 7878 | 8202
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.05 | 2604 | 6810 | 7090 | 7382
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.055 | 2498 | 6191 | 6445 | 6711
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.06 | 2397 | 5675 | 5908 | 6151
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.065 | 2303 | 5238 | 5454 | 5678
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00434 | 0.00907 | 0.00345 | 0.00203 | 0.0029 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.39631 | 4.0276 | 171.072 | 0.07 | 2214 | 4864 | 5064 | 5273
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.025 | 3080 | 12960 | 13510 | 14084
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.03 | 2938 | 10800 | 11258 | 11737
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.035 | 2805 | 9257 | 9650 | 10060
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.04 | 2680 | 8100 | 8444 | 8802
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.045 | 2563 | 7200 | 7506 | 7824
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.05 | 2453 | 6480 | 6755 | 7042
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.055 | 2350 | 5891 | 6141 | 6402
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.06 | 2253 | 5400 | 5629 | 5868
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.065 | 2162 | 4984 | 5196 | 5417
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00871 | 0.00332 | 0.00203 | 0.00279 | 0.00292 | 0.00698 | 0.00698 | 0.00203 | 0.00203 | 0.00203 | 0.40373 | 4.1609 | 174.672 | 0.07 | 2077 | 4628 | 4825 | 5030
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.025 | 2894 | 12236 | 12778 | 13343
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.03 | 2756 | 10197 | 10648 | 11119
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.035 | 2627 | 8740 | 9127 | 9531
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.04 | 2506 | 7648 | 7986 | 8340
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.045 | 2393 | 6798 | 7099 | 7413
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.05 | 2287 | 6118 | 6389 | 6672
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.055 | 2188 | 5562 | 5808 | 6065
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.06 | 2095 | 5098 | 5324 | 5560
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.065 | 2008 | 4706 | 4915 | 5132
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.0032 | 0.00202 | 0.00268 | 0.00282 | 0.00671 | 0.00671 | 0.00202 | 0.00202 | 0.00202 | 0.4186 | 4.3344 | 178.272 | 0.07 | 1926 | 4370 | 4564 | 4765
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.025 | 2662 | 11327 | 11860 | 12418
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.03 | 2528 | 9439 | 9883 | 10349
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.035 | 2403 | 8091 | 8472 | 8870
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.04 | 2287 | 7079 | 7413 | 7762
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.045 | 2178 | 6293 | 6589 | 6899
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.05 | 2077 | 5663 | 5930 | 6209
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.055 | 1983 | 5149 | 5391 | 5645
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.06 | 1895 | 4720 | 4942 | 5174
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.065 | 1813 | 4356 | 4562 | 4776
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00387 | 0.00806 | 0.00308 | 0.00201 | 0.00259 | 0.00271 | 0.00646 | 0.00646 | 0.00202 | 0.00202 | 0.00202 | 0.45049 | 4.5977 | 181.872 | 0.07 | 1736 | 4045 | 4236 | 4435
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.025 | 2557 | 10901 | 11425 | 11973
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.055 | 1896 | 4955 | 5193 | 5442
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.06 | 1811 | 4542 | 4760 | 4989
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.065 | 1731 | 4193 | 4394 | 4605
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.07 | 1657 | 3893 | 4080 | 4276
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.025 | 2452 | 10476 | 10990 | 11530
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.03 | 2324 | 8730 | 9159 | 9608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.035 | 2206 | 7483 | 7850 | 8235
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.04 | 2095 | 6548 | 6869 | 7206
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.045 | 1993 | 5820 | 6106 | 6405
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.05 | 1898 | 5238 | 5495 | 5765
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.055 | 1809 | 4762 | 4996 | 5241
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.06 | 1727 | 4365 | 4579 | 4804
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.065 | 1650 | 4029 | 4227 | 4434
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00287 | 0.002 | 0.00241 | 0.00253 | 0.00601 | 0.00601 | 0.002 | 0.002 | 0.002 | 0.44918 | 4.7932 | 189.072 | 0.07 | 1578 | 3742 | 3925 | 4118
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.025 | 2354 | 10074 | 10579 | 11109
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.03 | 2229 | 8395 | 8816 | 9257
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.035 | 2113 | 7196 | 7556 | 7935
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.04 | 2006 | 6296 | 6612 | 6943
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.045 | 1906 | 5597 | 5877 | 6172
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.05 | 1813 | 5037 | 5289 | 5554
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.055 | 1727 | 4579 | 4808 | 5049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.06 | 1647 | 4197 | 4408 | 4629
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.065 | 1573 | 3875 | 4069 | 4273
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00349 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.00245 | 0.00581 | 0.00581 | 0.002 | 0.002 | 0.002 | 0.44883 | 4.8924 | 192.672 | 0.07 | 1503 | 3598 | 3778 | 3967
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.025 | 2261 | 9692 | 10188 | 10709
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.03 | 2138 | 8077 | 8490 | 8924
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.035 | 2025 | 6923 | 7277 | 7649
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.04 | 1921 | 6058 | 6367 | 6693
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.045 | 1824 | 5384 | 5660 | 5950
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.05 | 1734 | 4846 | 5094 | 5355
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.055 | 1651 | 4405 | 4631 | 4868
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.06 | 1573 | 4038 | 4245 | 4462
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.065 | 1501 | 3728 | 3918 | 4119
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.002 | 0.00226 | 0.00237 | 0.00562 | 0.00562 | 0.002 | 0.002 | 0.002 | 0.44873 | 4.9929 | 196.272 | 0.07 | 1434 | 3461 | 3639 | 3825
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.025 | 2173 | 9330 | 9817 | 10330
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.035 | 1943 | 6664 | 7012 | 7378
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.04 | 1841 | 5831 | 6136 | 6456
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.045 | 1747 | 5183 | 5454 | 5739
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.05 | 1659 | 4665 | 4908 | 5165
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.055 | 1578 | 4241 | 4462 | 4695
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.06 | 1503 | 3887 | 4090 | 4304
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.065 | 1433 | 3588 | 3776 | 3973
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.07 | 1368 | 3332 | 3506 | 3689
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.025 | 2085 | 8968 | 9447 | 9951
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.03 | 1968 | 7473 | 7872 | 8292
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.035 | 1861 | 6406 | 6748 | 7108
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.04 | 1762 | 5605 | 5904 | 6219
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.045 | 1670 | 4982 | 5248 | 5528
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.05 | 1585 | 4484 | 4723 | 4975
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.055 | 1506 | 4076 | 4294 | 4523
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.06 | 1434 | 3737 | 3936 | 4146
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.065 | 1366 | 3449 | 3633 | 3827
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00656 | 0.00253 | 0.00199 | 0.00212 | 0.00223 | 0.00527 | 0.00527 | 0.00199 | 0.00199 | 0.00199 | 0.44929 | 5.1983 | 203.472 | 0.07 | 1303 | 3203 | 3374 | 3554
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.025 | 2007 | 8642 | 9112 | 9608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.03 | 1893 | 7201 | 7593 | 8007
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.035 | 1788 | 6173 | 6509 | 6863
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.04 | 1691 | 5401 | 5695 | 6005
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.045 | 1601 | 4801 | 5062 | 5338
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.05 | 1519 | 4321 | 4556 | 4804
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.055 | 1442 | 3928 | 4142 | 4367
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.06 | 1372 | 3601 | 3797 | 4003
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.065 | 1306 | 3324 | 3505 | 3695
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.0037 | 0.00307 | 0.00635 | 0.00245 | 0.00199 | 0.00206 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.45004 | 5.3039 | 207.072 | 0.07 | 1246 | 3086 | 3254 | 3431
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.025 | 1928 | 8315 | 8778 | 9266
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.03 | 1817 | 6929 | 7315 | 7721
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.035 | 1714 | 5940 | 6270 | 6618
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.04 | 1620 | 5197 | 5486 | 5791
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.045 | 1533 | 4620 | 4876 | 5148
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.05 | 1453 | 4158 | 4389 | 4633
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.055 | 1379 | 3780 | 3990 | 4212
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.06 | 1310 | 3465 | 3657 | 3861
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.065 | 1247 | 3198 | 3376 | 3564
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.0021 | 0.00496 | 0.00496 | 0.00198 | 0.00198 | 0.00198 | 0.45108 | 5.4113 | 210.672 | 0.07 | 1188 | 2970 | 3135 | 3309
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.025 | 1854 | 8005 | 8460 | 8940
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.035 | 1645 | 5718 | 6043 | 6385
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.04 | 1553 | 5003 | 5287 | 5587
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.045 | 1468 | 4447 | 4700 | 4966
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.05 | 1390 | 4003 | 4230 | 4470
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.055 | 1319 | 3639 | 3845 | 4063
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.06 | 1252 | 3336 | 3525 | 3725
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.065 | 1191 | 3079 | 3254 | 3438
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.07 | 1134 | 2859 | 3021 | 3193
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.025 | 1781 | 7696 | 8142 | 8615
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.03 | 1674 | 6413 | 6785 | 7179
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.035 | 1576 | 5497 | 5816 | 6153
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.04 | 1487 | 4810 | 5089 | 5384
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.045 | 1404 | 4275 | 4524 | 4786
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.05 | 1329 | 3848 | 4071 | 4307
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.055 | 1259 | 3498 | 3701 | 3916
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.06 | 1195 | 3207 | 3393 | 3590
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.065 | 1135 | 2960 | 3132 | 3313
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00198 | 0.00468 | 0.00468 | 0.00197 | 0.00197 | 0.00197 | 0.45478 | 5.637 | 217.872 | 0.07 | 1080 | 2749 | 2908 | 3077
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.025 | 1711 | 7402 | 7841 | 8306
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.03 | 1607 | 6168 | 6534 | 6922
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.035 | 1511 | 5287 | 5601 | 5933
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.04 | 1424 | 4626 | 4901 | 5191
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.045 | 1344 | 4112 | 4356 | 4614
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.05 | 1270 | 3701 | 3921 | 4153
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.055 | 1203 | 3365 | 3564 | 3775
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.06 | 1140 | 3084 | 3267 | 3461
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.065 | 1083 | 2847 | 3016 | 3195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00565 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00455 | 0.00455 | 0.00197 | 0.00197 | 0.00197 | 0.45814 | 5.76 | 221.472 | 0.07 | 1030 | 2644 | 2800 | 2966
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.025 | 1642 | 7110 | 7541 | 7999
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.03 | 1540 | 5925 | 6284 | 6666
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.035 | 1447 | 5079 | 5387 | 5713
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.04 | 1362 | 4444 | 4713 | 4999
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.045 | 1284 | 3950 | 4190 | 4444
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.05 | 1213 | 3555 | 3771 | 3999
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.055 | 1147 | 3232 | 3428 | 3636
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.06 | 1087 | 2962 | 3142 | 3333
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.065 | 1031 | 2735 | 2900 | 3076
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00443 | 0.00443 | 0.00197 | 0.00197 | 0.00197 | 0.46244 | 5.8895 | 225.072 | 0.07 | 980 | 2539 | 2693 | 2857
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.025 | 1574 | 6782 | 7244 | 7694
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.03 | 1474 | 5654 | 6037 | 6412
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.035 | 1384 | 4848 | 5174 | 5496
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.04 | 1301 | 4243 | 4528 | 4809
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.045 | 1225 | 3773 | 4024 | 4275
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.05 | 1156 | 3397 | 3622 | 3847
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.055 | 1092 | 3088 | 3293 | 3497
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.06 | 1034 | 2831 | 3018 | 3206
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.065 | 981 | 2615 | 2786 | 2959
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.07 | 931 | 2428 | 2587 | 2748
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.025 | 1510 | 6325 | 6962 | 7405
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.03 | 1412 | 5286 | 5802 | 6171
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.035 | 1324 | 4542 | 4973 | 5289
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.04 | 1243 | 3983 | 4351 | 4628
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.045 | 1170 | 3546 | 3868 | 4114
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.05 | 1102 | 3197 | 3481 | 3703
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.055 | 1041 | 2910 | 3165 | 3366
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.06 | 985 | 2670 | 2901 | 3086
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.065 | 933 | 2467 | 2678 | 2848
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.0042 | 0.0042 | 0.00196 | 0.00196 | 0.00196 | 0.47439 | 6.1731 | 232.272 | 0.07 | 885 | 2292 | 2486 | 2645
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.025 | 1444 | 5833 | 6672 | 7108
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.03 | 1349 | 4890 | 5560 | 5923
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.035 | 1263 | 4213 | 4766 | 5077
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.04 | 1184 | 3702 | 4170 | 4442
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.045 | 1113 | 3303 | 3707 | 3949
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.05 | 1048 | 2981 | 3336 | 3554
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.055 | 988 | 2717 | 3033 | 3231
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.06 | 934 | 2496 | 2780 | 2962
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.065 | 884 | 2309 | 2566 | 2734
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00297 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00409 | 0.00409 | 0.00196 | 0.00196 | 0.00196 | 0.48305 | 6.334 | 235.872 | 0.07 | 839 | 2147 | 2383 | 2539
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.025 | 1375 | 5284 | 6365 | 6794
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.03 | 1282 | 4448 | 5304 | 5662
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.035 | 1198 | 3845 | 4547 | 4853
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.04 | 1122 | 3389 | 3978 | 4246
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.045 | 1053 | 3031 | 3536 | 3775
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.05 | 990 | 2742 | 3183 | 3397
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.055 | 933 | 2504 | 2893 | 3088
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.06 | 881 | 2304 | 2652 | 2831
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.065 | 833 | 2134 | 2448 | 2613
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00399 | 0.00399 | 0.00195 | 0.00195 | 0.00195 | 0.49486 | 6.5172 | 239.472 | 0.07 | 789 | 1987 | 2273 | 2427
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.025 | 1305 | 4703 | 6057 | 6479
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.03 | 1215 | 3981 | 5047 | 5399
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.035 | 1134 | 3457 | 4326 | 4628
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.04 | 1060 | 3059 | 3786 | 4049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.045 | 993 | 2744 | 3365 | 3599
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.05 | 933 | 2490 | 3028 | 3239
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.055 | 878 | 2279 | 2753 | 2945
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.06 | 828 | 2101 | 2524 | 2699
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.065 | 782 | 1948 | 2330 | 2492
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.07 | 740 | 1817 | 2163 | 2314
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.025 | 1226 | 3973 | 5693 | 6117
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.03 | 1139 | 3395 | 4745 | 5097
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.035 | 1060 | 2971 | 4068 | 4369
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.04 | 989 | 2646 | 3560 | 3823
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.045 | 925 | 2387 | 3164 | 3398
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.05 | 867 | 2175 | 2848 | 3058
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.055 | 815 | 1998 | 2589 | 2780
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.06 | 767 | 1848 | 2374 | 2549
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.065 | 724 | 1719 | 2192 | 2353
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53663 | 7.0078 | 246.672 | 0.07 | 684 | 1606 | 2035 | 2185
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.025 | 1156 | 3288 | 5097 | 5789
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.03 | 1071 | 2845 | 4273 | 4825
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.035 | 995 | 2515 | 3682 | 4135
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.04 | 926 | 2258 | 3237 | 3618
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.045 | 865 | 2051 | 2888 | 3216
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.05 | 809 | 1879 | 2608 | 2895
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.055 | 759 | 1734 | 2378 | 2632
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.06 | 714 | 1611 | 2185 | 2412
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.065 | 673 | 1502 | 2021 | 2227
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00224 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00371 | 0.00371 | 0.00195 | 0.00195 | 0.00195 | 0.56133 | 7.2804 | 250.272 | 0.07 | 636 | 1408 | 1880 | 2068
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.025 | 1077 | 2439 | 4368 | 5421
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.03 | 995 | 2164 | 3698 | 4518
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.035 | 922 | 1951 | 3213 | 3872
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.04 | 856 | 1779 | 2844 | 3388
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.045 | 798 | 1637 | 2552 | 3012
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.05 | 745 | 1515 | 2316 | 2711
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.055 | 698 | 1409 | 2120 | 2464
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.06 | 655 | 1318 | 1955 | 2259
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.065 | 616 | 1237 | 1814 | 2085
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00362 | 0.00362 | 0.00195 | 0.00195 | 0.00195 | 0.59794 | 7.6308 | 253.872 | 0.07 | 581 | 1164 | 1692 | 1936
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.025 | 1008 | 1636 | 3678 | 5090
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.03 | 928 | 1520 | 3154 | 4241
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.035 | 858 | 1418 | 2768 | 3635
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.04 | 795 | 1327 | 2471 | 3181
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.045 | 739 | 1245 | 2233 | 2828
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.05 | 689 | 1170 | 2039 | 2545
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.055 | 644 | 1102 | 1876 | 2313
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.06 | 604 | 1041 | 1737 | 2121
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.065 | 567 | 986 | 1618 | 1958
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.07 | 534 | 934 | 1513 | 1818
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.025 | 971 | 1520 | 3354 | 4815
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.03 | 894 | 1420 | 2895 | 4024
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.035 | 825 | 1329 | 2556 | 3458
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.04 | 764 | 1246 | 2292 | 3033
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.045 | 709 | 1171 | 2080 | 2701
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.05 | 661 | 1103 | 1904 | 2435
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.055 | 617 | 1040 | 1757 | 2217
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.06 | 578 | 983 | 1631 | 2035
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.065 | 543 | 930 | 1522 | 1880
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00252 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63814 | 8.1244 | 261.072 | 0.07 | 511 | 882 | 1425 | 1747
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.025 | 934 | 1464 | 3002 | 4493
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.03 | 858 | 1366 | 2616 | 3772
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.035 | 791 | 1277 | 2326 | 3255
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.04 | 732 | 1196 | 2099 | 2864
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.045 | 679 | 1123 | 1914 | 2558
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.05 | 632 | 1057 | 1760 | 2312
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.055 | 590 | 996 | 1629 | 2109
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.06 | 552 | 940 | 1516 | 1939
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.065 | 518 | 889 | 1417 | 1795
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00338 | 0.00338 | 0.00194 | 0.00194 | 0.00194 | 0.6454 | 8.2917 | 264.672 | 0.07 | 488 | 843 | 1331 | 1671
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.025 | 896 | 1407 | 2624 | 4150
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.03 | 822 | 1311 | 2317 | 3505
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.035 | 757 | 1224 | 2081 | 3039
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.04 | 699 | 1146 | 1892 | 2686
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.045 | 648 | 1074 | 1737 | 2407
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.05 | 602 | 1010 | 1606 | 2182
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.055 | 562 | 951 | 1492 | 1996
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.06 | 525 | 897 | 1394 | 1839
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.065 | 493 | 848 | 1307 | 1705
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00331 | 0.00331 | 0.00194 | 0.00194 | 0.00194 | 0.65501 | 8.4754 | 268.272 | 0.07 | 463 | 803 | 1230 | 1589
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.025 | 859 | 1351 | 2239 | 3801
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.03 | 787 | 1257 | 2012 | 3234
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.035 | 723 | 1173 | 1830 | 2820
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.04 | 667 | 1096 | 1682 | 2504
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.045 | 618 | 1027 | 1556 | 2254
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.05 | 574 | 964 | 1448 | 2050
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.055 | 535 | 907 | 1353 | 1881
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.06 | 500 | 855 | 1269 | 1738
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.065 | 468 | 807 | 1195 | 1615
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.07 | 440 | 764 | 1128 | 1508

## interior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.02 | 3059 | 15324 | 15972 | 16647
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.025 | 2915 | 12259 | 12777 | 13317
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.03 | 2781 | 10216 | 10648 | 11098
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.035 | 2656 | 8756 | 9127 | 9512
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.04 | 2538 | 7662 | 7986 | 8323
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.045 | 2428 | 6811 | 7098 | 7398
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.05 | 2324 | 6130 | 6389 | 6659
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.02 | 2764 | 13942 | 14595 | 15279
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.025 | 2622 | 11154 | 11676 | 12224
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.03 | 2491 | 9295 | 9730 | 10186
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.035 | 2368 | 7967 | 8340 | 8731
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.04 | 2254 | 6971 | 7298 | 7640
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.045 | 2148 | 6196 | 6487 | 6791
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.05 | 2048 | 5577 | 5838 | 6112
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.02 | 2758 | 13913 | 14566 | 15251
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.025 | 2616 | 11130 | 11653 | 12200
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.03 | 2485 | 9275 | 9711 | 10167
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.035 | 2362 | 7950 | 8324 | 8715
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.04 | 2248 | 6956 | 7283 | 7625
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.045 | 2142 | 6183 | 6474 | 6778
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.05 | 2043 | 5565 | 5827 | 6100
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.02 | 2752 | 13884 | 14537 | 15222
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.025 | 2610 | 11107 | 11630 | 12177
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.035 | 2356 | 7934 | 8307 | 8698
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.04 | 2242 | 6942 | 7269 | 7611
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.045 | 2136 | 6171 | 6461 | 6765
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.05 | 2037 | 5554 | 5815 | 6089
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.02 | 2746 | 13855 | 14509 | 15193
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.025 | 2604 | 11084 | 11607 | 12154
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.03 | 2473 | 9237 | 9672 | 10129
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.035 | 2350 | 7917 | 8291 | 8682
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.04 | 2236 | 6927 | 7254 | 7597
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.045 | 2130 | 6158 | 6448 | 6752
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.05 | 2032 | 5542 | 5803 | 6077
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.02 | 2542 | 12830 | 13437 | 14072
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.025 | 2411 | 10264 | 10749 | 11258
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.03 | 2289 | 8553 | 8958 | 9381
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.035 | 2176 | 7331 | 7678 | 8041
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.04 | 2070 | 6415 | 6718 | 7036
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.045 | 1972 | 5702 | 5972 | 6254
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.05 | 1880 | 5132 | 5375 | 5629
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.02 | 2284 | 11570 | 12179 | 12820
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.025 | 2154 | 9256 | 9743 | 10256
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.035 | 1925 | 6612 | 6960 | 7326
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.04 | 1823 | 5785 | 6090 | 6410
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.045 | 1729 | 5142 | 5413 | 5698
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.05 | 1642 | 4628 | 4872 | 5128
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.02 | 2270 | 11502 | 12111 | 12752
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.025 | 2141 | 9202 | 9689 | 10202
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.035 | 1912 | 6573 | 6921 | 7287
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.04 | 1810 | 5751 | 6056 | 6376
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.045 | 1717 | 5112 | 5383 | 5668
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.05 | 1630 | 4601 | 4844 | 5101
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.02 | 2252 | 11412 | 12021 | 12663
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.025 | 2123 | 9130 | 9617 | 10130
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.03 | 2004 | 7608 | 8014 | 8442
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.035 | 1894 | 6521 | 6869 | 7236
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.04 | 1793 | 5706 | 6011 | 6331
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.045 | 1700 | 5072 | 5343 | 5628
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.05 | 1614 | 4565 | 4808 | 5065
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.02 | 2234 | 11323 | 11932 | 12574
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.025 | 2105 | 9058 | 9546 | 10059
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.03 | 1986 | 7549 | 7955 | 8383
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.035 | 1877 | 6470 | 6818 | 7185
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.04 | 1776 | 5661 | 5966 | 6287
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.045 | 1683 | 5032 | 5303 | 5588
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.05 | 1597 | 4529 | 4773 | 5030
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.02 | 1947 | 9874 | 10442 | 11042
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.025 | 1829 | 7899 | 8354 | 8834
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.03 | 1720 | 6583 | 6961 | 7362
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.035 | 1620 | 5642 | 5967 | 6310
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.04 | 1529 | 4937 | 5221 | 5521
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.045 | 1445 | 4389 | 4641 | 4908
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.05 | 1367 | 3950 | 4177 | 4417
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.02 | 1750 | 8506 | 9418 | 10018
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.025 | 1633 | 6830 | 7534 | 8014
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.03 | 1528 | 5709 | 6278 | 6679
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.035 | 1432 | 4906 | 5381 | 5725
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.04 | 1345 | 4302 | 4709 | 5009
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.045 | 1265 | 3831 | 4186 | 4452
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.05 | 1192 | 3453 | 3767 | 4007
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.02 | 1747 | 8471 | 9401 | 10002
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.025 | 1630 | 6803 | 7521 | 8001
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.03 | 1525 | 5687 | 6268 | 6668
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.035 | 1429 | 4888 | 5372 | 5715
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.04 | 1342 | 4287 | 4701 | 5001
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.045 | 1262 | 3818 | 4178 | 4445
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.05 | 1190 | 3442 | 3761 | 4001
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.02 | 1744 | 8435 | 9385 | 9986
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.025 | 1627 | 6776 | 7508 | 7989
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.03 | 1522 | 5665 | 6257 | 6657
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.035 | 1426 | 4870 | 5363 | 5706
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.04 | 1339 | 4271 | 4693 | 4993
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.045 | 1260 | 3805 | 4171 | 4438
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.05 | 1187 | 3430 | 3754 | 3994
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.02 | 1740 | 8399 | 9369 | 9970
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.025 | 1624 | 6748 | 7496 | 7976
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.03 | 1519 | 5644 | 6246 | 6646
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.035 | 1423 | 4852 | 5354 | 5697
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.04 | 1336 | 4256 | 4685 | 4985
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.045 | 1257 | 3792 | 4164 | 4431
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.05 | 1184 | 3419 | 3748 | 3988
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.02 | 1657 | 8171 | 8916 | 9478
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.025 | 1548 | 6552 | 7133 | 7583
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.03 | 1449 | 5471 | 5944 | 6319
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.035 | 1358 | 4697 | 5095 | 5416
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.04 | 1276 | 4116 | 4458 | 4739
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.045 | 1201 | 3663 | 3963 | 4213
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.05 | 1132 | 3300 | 3566 | 3791
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.02 | 1477 | 5900 | 7956 | 8516
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.025 | 1371 | 4821 | 6365 | 6813
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.03 | 1275 | 4089 | 5304 | 5677
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.035 | 1189 | 3557 | 4546 | 4866
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.04 | 1111 | 3152 | 3978 | 4258
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.045 | 1041 | 2832 | 3536 | 3785
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.05 | 977 | 2571 | 3182 | 3406
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.02 | 1468 | 5766 | 7904 | 8464
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.025 | 1362 | 4719 | 6323 | 6771
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.03 | 1266 | 4008 | 5270 | 5643
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.035 | 1180 | 3490 | 4517 | 4836
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.04 | 1103 | 3095 | 3952 | 4232
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.045 | 1033 | 2783 | 3513 | 3762
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.05 | 969 | 2529 | 3162 | 3386
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.02 | 1458 | 5633 | 7853 | 8412
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.025 | 1352 | 4617 | 6282 | 6730
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.03 | 1257 | 3926 | 5235 | 5608
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.035 | 1171 | 3423 | 4487 | 4807
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.04 | 1094 | 3039 | 3926 | 4206
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.045 | 1024 | 2734 | 3490 | 3739
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.05 | 961 | 2486 | 3141 | 3365
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.02 | 1444 | 5432 | 7777 | 8336
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.025 | 1339 | 4464 | 6221 | 6669
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.03 | 1244 | 3804 | 5185 | 5557
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.035 | 1158 | 3323 | 4444 | 4763
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.04 | 1081 | 2954 | 3888 | 4168
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.045 | 1012 | 2660 | 3456 | 3705
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.05 | 949 | 2421 | 3111 | 3334
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.02 | 1376 | 5362 | 7412 | 7938
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.025 | 1277 | 4392 | 5929 | 6351
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.03 | 1187 | 3732 | 4941 | 5292
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.035 | 1106 | 3252 | 4235 | 4536
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.04 | 1033 | 2885 | 3706 | 3969
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.045 | 967 | 2595 | 3294 | 3528
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.05 | 908 | 2359 | 2965 | 3175
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.02 | 1223 | 2974 | 5623 | 7088
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.025 | 1127 | 2571 | 4581 | 5670
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.03 | 1041 | 2279 | 3878 | 4725
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.035 | 964 | 2053 | 3368 | 4050
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.04 | 896 | 1872 | 2980 | 3544
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.045 | 835 | 1720 | 2674 | 3150
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.05 | 780 | 1592 | 2426 | 2835
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.02 | 1218 | 2880 | 5544 | 7057
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.025 | 1122 | 2499 | 4522 | 5645
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.03 | 1036 | 2222 | 3832 | 4704
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.035 | 959 | 2006 | 3330 | 4032
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.04 | 891 | 1832 | 2949 | 3528
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.045 | 830 | 1686 | 2648 | 3136
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.05 | 775 | 1562 | 2403 | 2823
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.02 | 1209 | 2723 | 5413 | 7006
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.025 | 1113 | 2380 | 4424 | 5605
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.03 | 1027 | 2126 | 3755 | 4670
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.035 | 951 | 1927 | 3268 | 4003
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.04 | 883 | 1765 | 2897 | 3503
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.045 | 822 | 1628 | 2604 | 3114
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.05 | 768 | 1512 | 2365 | 2802
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.02 | 1200 | 2566 | 5282 | 6955
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.025 | 1104 | 2260 | 4326 | 5564
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.03 | 1019 | 2031 | 3678 | 4637
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.035 | 943 | 1848 | 3206 | 3974
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.04 | 875 | 1698 | 2846 | 3478
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.045 | 815 | 1571 | 2560 | 3091
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.05 | 761 | 1461 | 2327 | 2782
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.02 | 1136 | 2482 | 5036 | 6585
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.025 | 1046 | 2179 | 4121 | 5268
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.03 | 965 | 1953 | 3501 | 4390
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.035 | 893 | 1775 | 3051 | 3763
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.04 | 829 | 1629 | 2706 | 3293
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.045 | 772 | 1505 | 2433 | 2927
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.05 | 721 | 1398 | 2211 | 2634
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.02 | 990 | 1531 | 2614 | 4832
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.025 | 903 | 1421 | 2308 | 3967
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.03 | 827 | 1322 | 2080 | 3378
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.035 | 760 | 1233 | 1898 | 2949
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.04 | 701 | 1152 | 1747 | 2621
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.045 | 649 | 1079 | 1618 | 2361
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.05 | 603 | 1013 | 1507 | 2149
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.02 | 981 | 1518 | 2441 | 4684
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.025 | 894 | 1408 | 2179 | 3859
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.03 | 818 | 1309 | 1979 | 3295
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.035 | 752 | 1220 | 1816 | 2883
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.04 | 693 | 1140 | 1678 | 2567
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.045 | 641 | 1067 | 1560 | 2316
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.05 | 595 | 1001 | 1457 | 2111
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.02 | 978 | 1514 | 2391 | 4642
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.025 | 891 | 1404 | 2142 | 3828
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.03 | 816 | 1306 | 1950 | 3271
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.035 | 749 | 1217 | 1792 | 2864
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.04 | 691 | 1136 | 1659 | 2552
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.045 | 639 | 1064 | 1543 | 2303
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.05 | 593 | 998 | 1443 | 2100
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.02 | 977 | 1512 | 2367 | 4621
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.025 | 890 | 1402 | 2123 | 3812
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.03 | 815 | 1304 | 1935 | 3260
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.035 | 748 | 1215 | 1780 | 2855
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.04 | 690 | 1135 | 1649 | 2544
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.045 | 638 | 1062 | 1535 | 2297
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.05 | 592 | 997 | 1436 | 2095
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.02 | 962 | 1486 | 2920 | 4957
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.025 | 879 | 1381 | 2520 | 4036
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.03 | 806 | 1286 | 2231 | 3414
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.035 | 742 | 1201 | 2009 | 2963
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.04 | 685 | 1124 | 1830 | 2621
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.045 | 635 | 1053 | 1682 | 2351
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.05 | 590 | 990 | 1557 | 2133
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.02 | 851 | 1324 | 1704 | 3093
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.025 | 771 | 1223 | 1588 | 2670
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.03 | 703 | 1132 | 1482 | 2366
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.035 | 642 | 1050 | 1387 | 2132
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.04 | 590 | 977 | 1300 | 1943
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.045 | 544 | 912 | 1222 | 1787
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.05 | 503 | 853 | 1150 | 1655
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.02 | 847 | 1318 | 1696 | 3013
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.025 | 767 | 1216 | 1580 | 2612
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.03 | 699 | 1126 | 1475 | 2321
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.035 | 639 | 1045 | 1380 | 2096
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.04 | 586 | 972 | 1293 | 1914
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.045 | 540 | 907 | 1215 | 1763
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.05 | 500 | 848 | 1143 | 1634
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.02 | 842 | 1312 | 1688 | 2933
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.025 | 763 | 1210 | 1572 | 2553
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.03 | 695 | 1120 | 1467 | 2276
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.035 | 635 | 1039 | 1372 | 2060
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.04 | 583 | 966 | 1286 | 1885
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.045 | 537 | 901 | 1208 | 1739
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.05 | 497 | 843 | 1136 | 1614
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.02 | 836 | 1303 | 1677 | 2813
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.025 | 757 | 1201 | 1561 | 2465
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.03 | 689 | 1111 | 1456 | 2208
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.035 | 629 | 1030 | 1362 | 2007
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.04 | 577 | 958 | 1276 | 1841
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.045 | 532 | 893 | 1197 | 1702
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.05 | 492 | 835 | 1126 | 1583

## exterior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.03 | 2703 | 9972 | 10405 | 10857
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.035 | 2578 | 8548 | 8919 | 9306
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.04 | 2462 | 7479 | 7804 | 8143
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.045 | 2352 | 6648 | 6937 | 7238
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.05 | 2250 | 5983 | 6243 | 6514
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.055 | 2154 | 5440 | 5676 | 5922
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.06 | 2064 | 4986 | 5203 | 5429
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.065 | 1979 | 4603 | 4803 | 5011
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.07 | 1900 | 4274 | 4459 | 4653
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.03 | 2420 | 9066 | 9502 | 9959
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.035 | 2298 | 7771 | 8145 | 8537
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.04 | 2185 | 6799 | 7127 | 7469
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.045 | 2080 | 6044 | 6335 | 6640
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.05 | 1982 | 5439 | 5701 | 5976
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.055 | 1891 | 4945 | 5183 | 5432
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.06 | 1806 | 4533 | 4751 | 4980
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.065 | 1726 | 4184 | 4386 | 4597
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.07 | 1652 | 3885 | 4072 | 4268
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.055 | 1896 | 4955 | 5193 | 5442
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.06 | 1811 | 4542 | 4760 | 4989
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.065 | 1731 | 4193 | 4394 | 4605
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.07 | 1657 | 3893 | 4080 | 4276
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.055 | 1896 | 4955 | 5193 | 5442
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.06 | 1811 | 4542 | 4760 | 4989
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.065 | 1731 | 4193 | 4394 | 4605
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.07 | 1657 | 3893 | 4080 | 4276
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.055 | 1896 | 4955 | 5193 | 5442
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.06 | 1811 | 4542 | 4760 | 4989
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.065 | 1731 | 4193 | 4394 | 4605
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.07 | 1657 | 3893 | 4080 | 4276
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.03 | 2294 | 8571 | 8976 | 9399
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.035 | 2181 | 7347 | 7693 | 8056
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.04 | 2075 | 6428 | 6732 | 7049
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.045 | 1977 | 5714 | 5984 | 6266
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.05 | 1885 | 5143 | 5385 | 5639
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.055 | 1800 | 4675 | 4896 | 5127
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.06 | 1720 | 4286 | 4488 | 4700
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.065 | 1645 | 3956 | 4143 | 4338
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.07 | 1575 | 3673 | 3847 | 4028
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.035 | 1943 | 6664 | 7012 | 7378
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.04 | 1841 | 5831 | 6136 | 6456
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.045 | 1747 | 5183 | 5454 | 5739
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.05 | 1659 | 4665 | 4908 | 5165
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.055 | 1578 | 4241 | 4462 | 4695
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.06 | 1503 | 3887 | 4090 | 4304
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.065 | 1433 | 3588 | 3776 | 3973
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.07 | 1368 | 3332 | 3506 | 3689
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.035 | 1943 | 6664 | 7012 | 7378
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.04 | 1841 | 5831 | 6136 | 6456
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.045 | 1747 | 5183 | 5454 | 5739
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.05 | 1659 | 4665 | 4908 | 5165
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.055 | 1578 | 4241 | 4462 | 4695
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.06 | 1503 | 3887 | 4090 | 4304
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.065 | 1433 | 3588 | 3776 | 3973
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.07 | 1368 | 3332 | 3506 | 3689
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.03 | 2049 | 7759 | 8165 | 8593
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.035 | 1939 | 6651 | 6999 | 7365
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.04 | 1837 | 5820 | 6124 | 6444
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.045 | 1742 | 5173 | 5444 | 5728
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.05 | 1655 | 4656 | 4899 | 5156
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.055 | 1574 | 4232 | 4454 | 4687
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.06 | 1499 | 3880 | 4083 | 4296
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.065 | 1429 | 3581 | 3769 | 3966
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.07 | 1364 | 3325 | 3499 | 3683
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.03 | 2049 | 7759 | 8165 | 8593
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.035 | 1939 | 6651 | 6999 | 7365
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.04 | 1837 | 5820 | 6124 | 6444
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.045 | 1742 | 5173 | 5444 | 5728
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.05 | 1655 | 4656 | 4899 | 5156
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.055 | 1574 | 4232 | 4454 | 4687
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.06 | 1499 | 3880 | 4083 | 4296
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.065 | 1429 | 3581 | 3769 | 3966
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.07 | 1364 | 3325 | 3499 | 3683
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.03 | 1959 | 7398 | 7777 | 8175
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.035 | 1855 | 6341 | 6666 | 7007
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.04 | 1760 | 5549 | 5833 | 6131
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.045 | 1671 | 4932 | 5185 | 5450
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.05 | 1588 | 4439 | 4666 | 4905
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.055 | 1512 | 4035 | 4242 | 4459
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.06 | 1441 | 3699 | 3888 | 4087
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.065 | 1375 | 3415 | 3589 | 3773
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.07 | 1313 | 3171 | 3333 | 3503
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.035 | 1645 | 5718 | 6043 | 6385
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.04 | 1553 | 5003 | 5287 | 5587
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.045 | 1468 | 4447 | 4700 | 4966
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.05 | 1390 | 4003 | 4230 | 4470
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.055 | 1319 | 3639 | 3845 | 4063
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.06 | 1252 | 3336 | 3525 | 3725
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.065 | 1191 | 3079 | 3254 | 3438
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.07 | 1134 | 2859 | 3021 | 3193
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.035 | 1645 | 5718 | 6043 | 6385
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.04 | 1553 | 5003 | 5287 | 5587
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.045 | 1468 | 4447 | 4700 | 4966
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.05 | 1390 | 4003 | 4230 | 4470
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.055 | 1319 | 3639 | 3845 | 4063
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.06 | 1252 | 3336 | 3525 | 3725
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.065 | 1191 | 3079 | 3254 | 3438
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.07 | 1134 | 2859 | 3021 | 3193
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.035 | 1641 | 5707 | 6032 | 6375
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.04 | 1550 | 4994 | 5278 | 5578
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.045 | 1465 | 4439 | 4691 | 4958
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.05 | 1387 | 3995 | 4222 | 4462
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.055 | 1315 | 3632 | 3838 | 4057
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.06 | 1249 | 3329 | 3518 | 3719
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.065 | 1188 | 3073 | 3248 | 3432
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.07 | 1131 | 2854 | 3016 | 3187
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.035 | 1641 | 5707 | 6032 | 6375
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.04 | 1550 | 4994 | 5278 | 5578
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.045 | 1465 | 4439 | 4691 | 4958
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.05 | 1387 | 3995 | 4222 | 4462
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.055 | 1315 | 3632 | 3838 | 4057
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.06 | 1249 | 3329 | 3518 | 3719
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.065 | 1188 | 3073 | 3248 | 3432
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.07 | 1131 | 2854 | 3016 | 3187
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.03 | 1670 | 6372 | 6727 | 7101
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.035 | 1576 | 5462 | 5766 | 6087
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.04 | 1489 | 4779 | 5045 | 5326
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.045 | 1409 | 4248 | 4484 | 4734
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.05 | 1335 | 3823 | 4036 | 4261
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.055 | 1267 | 3476 | 3669 | 3873
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.06 | 1204 | 3186 | 3363 | 3551
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.065 | 1146 | 2941 | 3105 | 3278
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.07 | 1092 | 2731 | 2883 | 3043
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.03 | 1480 | 5695 | 6058 | 6433
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.035 | 1389 | 4881 | 5192 | 5514
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.04 | 1306 | 4272 | 4543 | 4825
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.045 | 1230 | 3798 | 4038 | 4289
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.05 | 1161 | 3418 | 3635 | 3860
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.055 | 1097 | 3107 | 3304 | 3509
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.06 | 1039 | 2848 | 3029 | 3216
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.065 | 985 | 2630 | 2796 | 2969
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.07 | 936 | 2442 | 2596 | 2757
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.03 | 1474 | 5654 | 6037 | 6412
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.035 | 1384 | 4848 | 5174 | 5496
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.04 | 1301 | 4243 | 4528 | 4809
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.045 | 1225 | 3773 | 4024 | 4275
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.05 | 1156 | 3397 | 3622 | 3847
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.055 | 1092 | 3088 | 3293 | 3497
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.06 | 1034 | 2831 | 3018 | 3206
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.065 | 981 | 2615 | 2786 | 2959
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.07 | 931 | 2428 | 2587 | 2748
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.03 | 1469 | 5613 | 6016 | 6391
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.035 | 1378 | 4814 | 5156 | 5478
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.04 | 1295 | 4215 | 4512 | 4793
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.045 | 1220 | 3749 | 4011 | 4261
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.05 | 1151 | 3375 | 3610 | 3835
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.055 | 1087 | 3069 | 3281 | 3486
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.06 | 1029 | 2814 | 3008 | 3196
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.065 | 976 | 2599 | 2777 | 2950
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.07 | 927 | 2414 | 2578 | 2739
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.03 | 1463 | 5573 | 5995 | 6370
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.035 | 1372 | 4781 | 5139 | 5460
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.04 | 1290 | 4187 | 4496 | 4778
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.045 | 1214 | 3724 | 3997 | 4247
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.05 | 1145 | 3354 | 3597 | 3822
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.055 | 1082 | 3050 | 3270 | 3475
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.06 | 1024 | 2797 | 2998 | 3185
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.065 | 971 | 2584 | 2767 | 2940
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.07 | 922 | 2399 | 2569 | 2730
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.03 | 1398 | 5386 | 5719 | 6072
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.035 | 1312 | 4617 | 4902 | 5204
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.04 | 1234 | 4040 | 4289 | 4554
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.045 | 1163 | 3591 | 3812 | 4048
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.05 | 1097 | 3232 | 3431 | 3643
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.055 | 1037 | 2938 | 3119 | 3312
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.06 | 982 | 2693 | 2859 | 3036
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.065 | 932 | 2486 | 2639 | 2802
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.07 | 885 | 2308 | 2451 | 2602
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.03 | 1228 | 4095 | 5098 | 5449
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.035 | 1147 | 3551 | 4369 | 4671
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.04 | 1073 | 3139 | 3823 | 4087
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.045 | 1006 | 2813 | 3398 | 3633
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.05 | 945 | 2550 | 3059 | 3269
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.055 | 889 | 2333 | 2780 | 2972
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.06 | 839 | 2149 | 2549 | 2725
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.065 | 793 | 1992 | 2353 | 2515
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.07 | 751 | 1857 | 2185 | 2335
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.03 | 1215 | 3981 | 5047 | 5399
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.035 | 1134 | 3457 | 4326 | 4628
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.04 | 1060 | 3059 | 3786 | 4049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.045 | 993 | 2744 | 3365 | 3599
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.05 | 933 | 2490 | 3028 | 3239
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.055 | 878 | 2279 | 2753 | 2945
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.06 | 828 | 2101 | 2524 | 2699
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.065 | 782 | 1948 | 2330 | 2492
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.07 | 740 | 1817 | 2163 | 2314
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.03 | 1198 | 3828 | 4982 | 5333
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.035 | 1117 | 3331 | 4270 | 4571
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.04 | 1043 | 2952 | 3736 | 4000
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.045 | 977 | 2652 | 3321 | 3555
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.05 | 917 | 2409 | 2989 | 3200
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.055 | 863 | 2207 | 2717 | 2909
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.06 | 813 | 2036 | 2491 | 2666
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.065 | 768 | 1890 | 2299 | 2461
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.07 | 727 | 1763 | 2135 | 2285
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.03 | 1176 | 3637 | 4901 | 5252
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.035 | 1096 | 3173 | 4201 | 4502
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.04 | 1023 | 2819 | 3676 | 3939
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.045 | 958 | 2537 | 3267 | 3501
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.05 | 898 | 2308 | 2941 | 3151
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.055 | 845 | 2118 | 2673 | 2865
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.06 | 796 | 1956 | 2451 | 2626
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.065 | 751 | 1817 | 2262 | 2424
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.07 | 710 | 1697 | 2101 | 2251
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.03 | 1099 | 3325 | 4582 | 4913
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.035 | 1023 | 2907 | 3928 | 4211
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.04 | 955 | 2586 | 3437 | 3685
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.045 | 893 | 2331 | 3055 | 3275
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.05 | 838 | 2122 | 2749 | 2948
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.055 | 787 | 1948 | 2499 | 2680
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.06 | 741 | 1801 | 2291 | 2457
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.065 | 700 | 1675 | 2115 | 2268
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.07 | 662 | 1564 | 1964 | 2106
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.03 | 940 | 1665 | 3270 | 4290
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.035 | 869 | 1537 | 2862 | 3677
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.04 | 806 | 1427 | 2549 | 3218
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.045 | 750 | 1331 | 2300 | 2860
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.05 | 699 | 1246 | 2097 | 2574
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.055 | 654 | 1170 | 1926 | 2340
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.06 | 613 | 1102 | 1782 | 2145
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.065 | 576 | 1041 | 1658 | 1980
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.07 | 543 | 984 | 1549 | 1839
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.03 | 928 | 1520 | 3154 | 4241
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.035 | 858 | 1418 | 2768 | 3635
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.04 | 795 | 1327 | 2471 | 3181
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.045 | 739 | 1245 | 2233 | 2828
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.05 | 689 | 1170 | 2039 | 2545
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.055 | 644 | 1102 | 1876 | 2313
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.06 | 604 | 1041 | 1737 | 2121
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.065 | 567 | 986 | 1618 | 1958
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.07 | 534 | 934 | 1513 | 1818
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.03 | 925 | 1484 | 3124 | 4229
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.035 | 855 | 1388 | 2745 | 3625
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.04 | 792 | 1302 | 2451 | 3172
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.045 | 736 | 1223 | 2217 | 2820
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.05 | 686 | 1151 | 2025 | 2538
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.055 | 641 | 1085 | 1863 | 2307
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.06 | 601 | 1026 | 1726 | 2115
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.065 | 565 | 972 | 1608 | 1952
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.07 | 532 | 921 | 1504 | 1813
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.03 | 922 | 1464 | 3096 | 4211
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.035 | 852 | 1371 | 2721 | 3611
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.04 | 789 | 1286 | 2432 | 3159
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.045 | 734 | 1210 | 2200 | 2809
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.05 | 684 | 1139 | 2010 | 2529
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.055 | 639 | 1075 | 1851 | 2299
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.06 | 599 | 1017 | 1715 | 2108
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.065 | 563 | 963 | 1598 | 1945
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.07 | 530 | 913 | 1495 | 1807
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.03 | 908 | 1781 | 3261 | 4134
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.035 | 840 | 1624 | 2844 | 3543
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.04 | 780 | 1494 | 2525 | 3100
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.045 | 726 | 1384 | 2273 | 2756
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.05 | 677 | 1288 | 2067 | 2480
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.055 | 634 | 1204 | 1896 | 2255
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.06 | 595 | 1130 | 1751 | 2067
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.065 | 559 | 1063 | 1627 | 1908
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.07 | 527 | 1004 | 1520 | 1772
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.03 | 793 | 1266 | 2080 | 3290
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.035 | 729 | 1181 | 1886 | 2865
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.04 | 673 | 1105 | 1728 | 2541
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.045 | 623 | 1035 | 1595 | 2284
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.05 | 579 | 972 | 1482 | 2076
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.055 | 539 | 915 | 1383 | 1903
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.06 | 504 | 862 | 1296 | 1757
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.065 | 473 | 815 | 1219 | 1632
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.07 | 444 | 771 | 1149 | 1523
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.03 | 787 | 1257 | 2012 | 3234
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.035 | 723 | 1173 | 1830 | 2820
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.04 | 667 | 1096 | 1682 | 2504
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.045 | 618 | 1027 | 1556 | 2254
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.05 | 574 | 964 | 1448 | 2050
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.055 | 535 | 907 | 1353 | 1881
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.06 | 500 | 855 | 1269 | 1738
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.065 | 468 | 807 | 1195 | 1615
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.07 | 440 | 764 | 1128 | 1508
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.03 | 778 | 1245 | 1915 | 3155
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.035 | 715 | 1161 | 1752 | 2758
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.04 | 660 | 1084 | 1617 | 2453
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.045 | 610 | 1015 | 1501 | 2212
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.05 | 567 | 953 | 1400 | 2014
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.055 | 528 | 896 | 1311 | 1850
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.06 | 493 | 845 | 1232 | 1711
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.065 | 462 | 798 | 1162 | 1591
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.07 | 434 | 755 | 1098 | 1487
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.03 | 769 | 1231 | 1805 | 3065
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.035 | 706 | 1147 | 1663 | 2686
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.04 | 651 | 1071 | 1543 | 2395
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.045 | 602 | 1003 | 1438 | 2163
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.05 | 559 | 941 | 1346 | 1973
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.055 | 520 | 884 | 1263 | 1815
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.06 | 486 | 833 | 1190 | 1680
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.065 | 455 | 787 | 1124 | 1564
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.07 | 428 | 744 | 1063 | 1463

## 50%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | % change from normal
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | Very Slow | Slow | Moderate | Fast
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.03 | 2558 | 9512 | 9947 | 10402 | -0.053644 | -0.046129 | -0.044017 | -0.041908
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.035 | 2435 | 8153 | 8526 | 8916 | -0.055469 | -0.04621 | -0.044063 | -0.041908
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.04 | 2320 | 7134 | 7460 | 7801 | -0.057677 | -0.046129 | -0.04408 | -0.041999
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.045 | 2213 | 6342 | 6631 | 6935 | -0.059099 | -0.046029 | -0.044111 | -0.041862
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.05 | 2112 | 5707 | 5968 | 6241 | -0.061333 | -0.046131 | -0.044049 | -0.04191
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.055 | 2019 | 5189 | 5426 | 5674 | -0.062674 | -0.04614 | -0.044045 | -0.041878
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.06 | 1931 | 4756 | 4974 | 5201 | -0.064438 | -0.046129 | -0.044013 | -0.041997
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.065 | 1849 | 4390 | 4591 | 4801 | -0.06569 | -0.046274 | -0.044139 | -0.041908
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.49736 | 4.4671 | 185.472 | 0.07 | 1772 | 4077 | 4263 | 4458 | -0.067368 | -0.046093 | -0.043956 | -0.041908
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.03 | 2294 | 8651 | 9088 | 9547 | -0.052066 | -0.045775 | -0.04357 | -0.04137
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.035 | 2174 | 7415 | 7789 | 8183 | -0.05396 | -0.045811 | -0.043708 | -0.041467
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.04 | 2063 | 6488 | 6816 | 7160 | -0.055835 | -0.045742 | -0.043637 | -0.041371
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.045 | 1960 | 5767 | 6058 | 6365 | -0.057692 | -0.045831 | -0.043725 | -0.041416
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.05 | 1864 | 5190 | 5453 | 5728 | -0.059536 | -0.04578 | -0.043501 | -0.041499
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.055 | 1775 | 4718 | 4957 | 5207 | -0.061343 | -0.045905 | -0.043604 | -0.041421
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.06 | 1692 | 4325 | 4544 | 4773 | -0.063123 | -0.045886 | -0.04357 | -0.041566
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.065 | 1615 | 3993 | 4194 | 4406 | -0.064311 | -0.04565 | -0.043776 | -0.041549
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.4968 | 4.9346 | 185.472 | 0.07 | 1544 | 3707 | 3895 | 4092 | -0.065375 | -0.045817 | -0.043468 | -0.041237
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.03 | 2294 | 8651 | 9088 | 9547 | -0.054411 | -0.047771 | -0.045478 | -0.043195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.035 | 2174 | 7415 | 7789 | 8183 | -0.056424 | -0.047772 | -0.045583 | -0.043148
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.04 | 2063 | 6488 | 6816 | 7160 | -0.058421 | -0.047703 | -0.045512 | -0.043165
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.045 | 1960 | 5767 | 6058 | 6365 | -0.060403 | -0.047721 | -0.045533 | -0.043145
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.05 | 1864 | 5190 | 5453 | 5728 | -0.062374 | -0.047881 | -0.045343 | -0.04326
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.055 | 1775 | 4718 | 4957 | 5207 | -0.063819 | -0.04783 | -0.045446 | -0.043183
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.06 | 1692 | 4325 | 4544 | 4773 | -0.06571 | -0.047776 | -0.045378 | -0.043295
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.065 | 1615 | 3993 | 4194 | 4406 | -0.067013 | -0.047699 | -0.045517 | -0.043214
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.49645 | 4.9328 | 185.472 | 0.07 | 1544 | 3707 | 3895 | 4092 | -0.068196 | -0.047778 | -0.045343 | -0.043031
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.03 | 2294 | 8651 | 9088 | 9547 | -0.054411 | -0.047771 | -0.045478 | -0.043195
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.035 | 2174 | 7415 | 7789 | 8183 | -0.056424 | -0.047772 | -0.045583 | -0.043148
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.04 | 2063 | 6488 | 6816 | 7160 | -0.058421 | -0.047703 | -0.045512 | -0.043165
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.045 | 1960 | 5767 | 6058 | 6365 | -0.060403 | -0.047721 | -0.045533 | -0.043145
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.05 | 1864 | 5190 | 5453 | 5728 | -0.062374 | -0.047881 | -0.045343 | -0.04326
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.055 | 1775 | 4718 | 4957 | 5207 | -0.063819 | -0.04783 | -0.045446 | -0.043183
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.06 | 1692 | 4325 | 4544 | 4773 | -0.06571 | -0.047776 | -0.045378 | -0.043295
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.065 | 1615 | 3993 | 4194 | 4406 | -0.067013 | -0.047699 | -0.045517 | -0.043214
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.49607 | 4.9309 | 185.472 | 0.07 | 1544 | 3707 | 3895 | 4092 | -0.068196 | -0.047778 | -0.045343 | -0.043031
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.03 | 2294 | 8651 | 9088 | 9547 | -0.054411 | -0.047771 | -0.045478 | -0.043195
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.035 | 2174 | 7415 | 7789 | 8183 | -0.056424 | -0.047772 | -0.045583 | -0.043148
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.04 | 2063 | 6488 | 6816 | 7160 | -0.058421 | -0.047703 | -0.045512 | -0.043165
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.045 | 1960 | 5767 | 6058 | 6365 | -0.060403 | -0.047721 | -0.045533 | -0.043145
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.05 | 1864 | 5190 | 5453 | 5728 | -0.062374 | -0.047881 | -0.045343 | -0.04326
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.055 | 1775 | 4718 | 4957 | 5207 | -0.063819 | -0.04783 | -0.045446 | -0.043183
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.06 | 1692 | 4325 | 4544 | 4773 | -0.06571 | -0.047776 | -0.045378 | -0.043295
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.065 | 1615 | 3993 | 4194 | 4406 | -0.067013 | -0.047699 | -0.045517 | -0.043214
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.49567 | 4.929 | 185.472 | 0.07 | 1544 | 3707 | 3895 | 4092 | -0.068196 | -0.047778 | -0.045343 | -0.043031
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.03 | 2173 | 8175 | 8580 | 9006 | -0.052746 | -0.046202 | -0.044118 | -0.041813
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.035 | 2061 | 7007 | 7355 | 7719 | -0.055021 | -0.046277 | -0.043936 | -0.041832
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.04 | 1957 | 6131 | 6435 | 6754 | -0.056867 | -0.046204 | -0.044118 | -0.04185
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.045 | 1861 | 5450 | 5720 | 6004 | -0.058675 | -0.046202 | -0.044118 | -0.041813
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.05 | 1771 | 4905 | 5148 | 5403 | -0.060477 | -0.046276 | -0.044011 | -0.041851
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.055 | 1688 | 4459 | 4680 | 4912 | -0.062222 | -0.046203 | -0.044118 | -0.041935
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.06 | 1610 | 4087 | 4290 | 4503 | -0.063953 | -0.04643 | -0.044118 | -0.041915
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.065 | 1538 | 3773 | 3960 | 4157 | -0.065046 | -0.046259 | -0.044171 | -0.041724
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.49501 | 4.8407 | 199.872 | 0.07 | 1471 | 3504 | 3677 | 3860 | -0.066032 | -0.046011 | -0.04419 | -0.041708
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.03 | 1940 | 7389 | 7795 | 8223 | -0.055041 | -0.049646 | -0.047182 | -0.044726
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.035 | 1831 | 6333 | 6681 | 7049 | -0.057643 | -0.04967 | -0.047205 | -0.044592
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.04 | 1731 | 5542 | 5846 | 6168 | -0.05975 | -0.049563 | -0.047262 | -0.04461
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.045 | 1639 | 4926 | 5197 | 5482 | -0.06182 | -0.049585 | -0.047121 | -0.044781
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.05 | 1554 | 4433 | 4677 | 4934 | -0.063291 | -0.049732 | -0.047066 | -0.044724
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.055 | 1475 | 4030 | 4252 | 4485 | -0.065272 | -0.049752 | -0.047064 | -0.044728
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.06 | 1403 | 3694 | 3897 | 4112 | -0.066534 | -0.049653 | -0.047188 | -0.04461
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.065 | 1335 | 3410 | 3598 | 3795 | -0.068388 | -0.04961 | -0.04714 | -0.044802
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.495 | 5.3502 | 199.872 | 0.07 | 1273 | 3167 | 3341 | 3524 | -0.069444 | -0.04952 | -0.047062 | -0.044728
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.03 | 1940 | 7389 | 7795 | 8223 | -0.055041 | -0.049646 | -0.047182 | -0.044726
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.035 | 1831 | 6333 | 6681 | 7049 | -0.057643 | -0.04967 | -0.047205 | -0.044592
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.04 | 1731 | 5542 | 5846 | 6168 | -0.05975 | -0.049563 | -0.047262 | -0.04461
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.045 | 1639 | 4926 | 5197 | 5482 | -0.06182 | -0.049585 | -0.047121 | -0.044781
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.05 | 1554 | 4433 | 4677 | 4934 | -0.063291 | -0.049732 | -0.047066 | -0.044724
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.055 | 1475 | 4030 | 4252 | 4485 | -0.065272 | -0.049752 | -0.047064 | -0.044728
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.06 | 1403 | 3694 | 3897 | 4112 | -0.066534 | -0.049653 | -0.047188 | -0.04461
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.065 | 1335 | 3410 | 3598 | 3795 | -0.068388 | -0.04961 | -0.04714 | -0.044802
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.49526 | 5.3516 | 199.872 | 0.07 | 1273 | 3167 | 3341 | 3524 | -0.069444 | -0.04952 | -0.047062 | -0.044728
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.03 | 1940 | 7389 | 7795 | 8223 | -0.053197 | -0.047687 | -0.045315 | -0.043058
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.035 | 1831 | 6333 | 6681 | 7049 | -0.055699 | -0.047812 | -0.045435 | -0.042906
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.04 | 1731 | 5542 | 5846 | 6168 | -0.057703 | -0.047766 | -0.045395 | -0.042831
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.045 | 1639 | 4926 | 5197 | 5482 | -0.059127 | -0.047748 | -0.045371 | -0.042947
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.05 | 1554 | 4433 | 4677 | 4934 | -0.061027 | -0.047895 | -0.045315 | -0.043057
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.055 | 1475 | 4030 | 4252 | 4485 | -0.062897 | -0.047732 | -0.045352 | -0.043098
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.06 | 1403 | 3694 | 3897 | 4112 | -0.064043 | -0.047938 | -0.045555 | -0.042831
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.065 | 1335 | 3410 | 3598 | 3795 | -0.06578 | -0.047752 | -0.04537 | -0.043116
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.49519 | 5.3512 | 199.872 | 0.07 | 1273 | 3167 | 3341 | 3524 | -0.066716 | -0.047519 | -0.045156 | -0.043171
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.03 | 1940 | 7389 | 7795 | 8223 | -0.053197 | -0.047687 | -0.045315 | -0.043058
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.035 | 1831 | 6333 | 6681 | 7049 | -0.055699 | -0.047812 | -0.045435 | -0.042906
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.04 | 1731 | 5542 | 5846 | 6168 | -0.057703 | -0.047766 | -0.045395 | -0.042831
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.045 | 1639 | 4926 | 5197 | 5482 | -0.059127 | -0.047748 | -0.045371 | -0.042947
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.05 | 1554 | 4433 | 4677 | 4934 | -0.061027 | -0.047895 | -0.045315 | -0.043057
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.055 | 1475 | 4030 | 4252 | 4485 | -0.062897 | -0.047732 | -0.045352 | -0.043098
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.06 | 1403 | 3694 | 3897 | 4112 | -0.064043 | -0.047938 | -0.045555 | -0.042831
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.065 | 1335 | 3410 | 3598 | 3795 | -0.06578 | -0.047752 | -0.04537 | -0.043116
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.49522 | 5.3514 | 199.872 | 0.07 | 1273 | 3167 | 3341 | 3524 | -0.066716 | -0.047519 | -0.045156 | -0.043171
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.03 | 1853 | 7041 | 7420 | 7819 | -0.054109 | -0.048256 | -0.045905 | -0.043547
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.035 | 1751 | 6035 | 6360 | 6702 | -0.056065 | -0.048257 | -0.045905 | -0.043528
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.04 | 1657 | 5281 | 5565 | 5865 | -0.058523 | -0.048297 | -0.045945 | -0.043386
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.045 | 1570 | 4694 | 4947 | 5213 | -0.060443 | -0.048256 | -0.045902 | -0.043486
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.05 | 1490 | 4225 | 4452 | 4692 | -0.061713 | -0.048209 | -0.045864 | -0.043425
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.055 | 1416 | 3841 | 4047 | 4265 | -0.063492 | -0.048079 | -0.045969 | -0.043508
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.06 | 1347 | 3521 | 3710 | 3910 | -0.065232 | -0.048121 | -0.045782 | -0.043308
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.065 | 1283 | 3250 | 3425 | 3609 | -0.066909 | -0.048316 | -0.045695 | -0.043467
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.49794 | 5.2403 | 214.272 | 0.07 | 1224 | 3018 | 3180 | 3351 | -0.067784 | -0.04825 | -0.045905 | -0.043391
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.03 | 1647 | 6328 | 6706 | 7107 | -0.05616 | -0.051417 | -0.048794 | -0.04604
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.035 | 1549 | 5424 | 5748 | 6091 | -0.058359 | -0.051417 | -0.048817 | -0.046045
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.04 | 1459 | 4746 | 5030 | 5330 | -0.060528 | -0.051369 | -0.04861 | -0.046
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.045 | 1376 | 4219 | 4471 | 4738 | -0.06267 | -0.051271 | -0.048723 | -0.045912
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.05 | 1301 | 3797 | 4024 | 4264 | -0.064029 | -0.051461 | -0.0487 | -0.046085
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.055 | 1231 | 3452 | 3658 | 3876 | -0.066717 | -0.051388 | -0.048635 | -0.046025
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.06 | 1167 | 3164 | 3353 | 3553 | -0.067891 | -0.051559 | -0.048794 | -0.046174
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.065 | 1108 | 2921 | 3095 | 3280 | -0.069689 | -0.051315 | -0.048863 | -0.045957
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.49867 | 5.7962 | 214.272 | 0.07 | 1054 | 2712 | 2874 | 3046 | -0.070547 | -0.051417 | -0.048659 | -0.046038
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.03 | 1647 | 6328 | 6706 | 7107 | -0.05616 | -0.051417 | -0.048794 | -0.04604
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.035 | 1549 | 5424 | 5748 | 6091 | -0.058359 | -0.051417 | -0.048817 | -0.046045
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.04 | 1459 | 4746 | 5030 | 5330 | -0.060528 | -0.051369 | -0.04861 | -0.046
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.045 | 1376 | 4219 | 4471 | 4738 | -0.06267 | -0.051271 | -0.048723 | -0.045912
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.05 | 1301 | 3797 | 4024 | 4264 | -0.064029 | -0.051461 | -0.0487 | -0.046085
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.055 | 1231 | 3452 | 3658 | 3876 | -0.066717 | -0.051388 | -0.048635 | -0.046025
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.06 | 1167 | 3164 | 3353 | 3553 | -0.067891 | -0.051559 | -0.048794 | -0.046174
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.065 | 1108 | 2921 | 3095 | 3280 | -0.069689 | -0.051315 | -0.048863 | -0.045957
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.4995 | 5.801 | 214.272 | 0.07 | 1054 | 2712 | 2874 | 3046 | -0.070547 | -0.051417 | -0.048659 | -0.046038
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.03 | 1644 | 6317 | 6694 | 7095 | -0.056257 | -0.051217 | -0.048742 | -0.045986
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.035 | 1546 | 5414 | 5738 | 6081 | -0.057892 | -0.05134 | -0.04874 | -0.046118
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.04 | 1456 | 4737 | 5021 | 5321 | -0.060645 | -0.051462 | -0.048693 | -0.046074
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.045 | 1373 | 4211 | 4463 | 4730 | -0.062799 | -0.051363 | -0.048604 | -0.045986
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.05 | 1298 | 3790 | 4017 | 4257 | -0.064167 | -0.051314 | -0.048555 | -0.045944
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.055 | 1228 | 3445 | 3652 | 3870 | -0.06616 | -0.051487 | -0.048463 | -0.046093
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.06 | 1164 | 3158 | 3347 | 3547 | -0.068054 | -0.051367 | -0.048607 | -0.046249
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.065 | 1105 | 2915 | 3090 | 3275 | -0.069865 | -0.051416 | -0.048645 | -0.045746
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.50049 | 5.8068 | 214.272 | 0.07 | 1051 | 2707 | 2869 | 3041 | -0.070734 | -0.051507 | -0.04874 | -0.045811
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.03 | 1644 | 6317 | 6694 | 7095 | -0.056257 | -0.051217 | -0.048742 | -0.045986
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.035 | 1546 | 5414 | 5738 | 6081 | -0.057892 | -0.05134 | -0.04874 | -0.046118
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.04 | 1456 | 4737 | 5021 | 5321 | -0.060645 | -0.051462 | -0.048693 | -0.046074
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.045 | 1373 | 4211 | 4463 | 4730 | -0.062799 | -0.051363 | -0.048604 | -0.045986
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.05 | 1298 | 3790 | 4017 | 4257 | -0.064167 | -0.051314 | -0.048555 | -0.045944
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.055 | 1228 | 3445 | 3652 | 3870 | -0.06616 | -0.051487 | -0.048463 | -0.046093
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.06 | 1164 | 3158 | 3347 | 3547 | -0.068054 | -0.051367 | -0.048607 | -0.046249
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.065 | 1105 | 2915 | 3090 | 3275 | -0.069865 | -0.051416 | -0.048645 | -0.045746
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.5018 | 5.8143 | 214.272 | 0.07 | 1051 | 2707 | 2869 | 3041 | -0.070734 | -0.051507 | -0.04874 | -0.045811
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.03 | 1575 | 6042 | 6396 | 6771 | -0.056886 | -0.051789 | -0.049205 | -0.046472
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.035 | 1483 | 5179 | 5482 | 5804 | -0.05901 | -0.051813 | -0.049254 | -0.046493
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.04 | 1398 | 4531 | 4797 | 5079 | -0.061115 | -0.051894 | -0.049158 | -0.046376
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.045 | 1320 | 4028 | 4264 | 4514 | -0.063165 | -0.051789 | -0.049063 | -0.046472
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.05 | 1248 | 3625 | 3838 | 4063 | -0.065169 | -0.051792 | -0.049058 | -0.046468
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.055 | 1182 | 3296 | 3489 | 3693 | -0.067088 | -0.051784 | -0.04906 | -0.046476
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.06 | 1121 | 3021 | 3198 | 3386 | -0.068937 | -0.051789 | -0.049063 | -0.046466
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.065 | 1065 | 2789 | 2952 | 3125 | -0.070681 | -0.051683 | -0.049275 | -0.046675
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.51142 | 5.7014 | 228.672 | 0.07 | 1013 | 2589 | 2741 | 2902 | -0.072344 | -0.051996 | -0.049254 | -0.046336
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.03 | 1394 | 5065 | 5745 | 6119 | -0.058108 | -0.11062 | -0.051667 | -0.048811
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.035 | 1305 | 4362 | 4924 | 5245 | -0.060475 | -0.10633 | -0.051618 | -0.048785
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.04 | 1224 | 3832 | 4309 | 4590 | -0.062787 | -0.103 | -0.051508 | -0.048705
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.045 | 1150 | 3419 | 3830 | 4080 | -0.065041 | -0.099789 | -0.051511 | -0.048729
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.05 | 1083 | 3086 | 3447 | 3672 | -0.067183 | -0.097133 | -0.051719 | -0.048705
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.055 | 1022 | 2812 | 3133 | 3338 | -0.068368 | -0.094947 | -0.051755 | -0.048732
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.06 | 966 | 2583 | 2872 | 3060 | -0.07026 | -0.093048 | -0.051832 | -0.048507
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.065 | 914 | 2390 | 2651 | 2824 | -0.072081 | -0.091255 | -0.05186 | -0.048838
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.51413 | 6.3182 | 228.672 | 0.07 | 867 | 2222 | 2462 | 2623 | -0.073718 | -0.09009 | -0.051618 | -0.048604
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.03 | 1389 | 5024 | 5725 | 6100 | -0.057666 | -0.11143 | -0.051681 | -0.048659
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.035 | 1300 | 4328 | 4907 | 5229 | -0.060694 | -0.10726 | -0.051604 | -0.048581
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.04 | 1219 | 3804 | 4294 | 4575 | -0.063028 | -0.10346 | -0.051678 | -0.048659
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.045 | 1145 | 3394 | 3817 | 4067 | -0.065306 | -0.10045 | -0.051441 | -0.048655
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.05 | 1078 | 3065 | 3435 | 3660 | -0.067474 | -0.097733 | -0.051629 | -0.048609
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.055 | 1017 | 2793 | 3123 | 3327 | -0.068681 | -0.095531 | -0.051625 | -0.048613
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.06 | 961 | 2566 | 2863 | 3050 | -0.0706 | -0.093606 | -0.051359 | -0.048659
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.065 | 910 | 2374 | 2642 | 2815 | -0.072375 | -0.092161 | -0.051687 | -0.048665
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.51732 | 6.3378 | 228.672 | 0.07 | 863 | 2208 | 2454 | 2614 | -0.07304 | -0.09061 | -0.051411 | -0.048763
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.03 | 1383 | 4983 | 5706 | 6081 | -0.058543 | -0.11224 | -0.051529 | -0.048506
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.035 | 1295 | 4295 | 4891 | 5212 | -0.060232 | -0.10781 | -0.051396 | -0.048558
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.04 | 1214 | 3776 | 4280 | 4561 | -0.062548 | -0.10415 | -0.051418 | -0.048404
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.045 | 1141 | 3370 | 3804 | 4054 | -0.064754 | -0.10109 | -0.051608 | -0.04858
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.05 | 1074 | 3043 | 3424 | 3648 | -0.066898 | -0.09837 | -0.051524 | -0.048761
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.055 | 1013 | 2774 | 3112 | 3317 | -0.068077 | -0.096123 | -0.051509 | -0.04848
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.06 | 957 | 2549 | 2853 | 3040 | -0.069971 | -0.094172 | -0.051529 | -0.048811
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.065 | 906 | 2359 | 2634 | 2806 | -0.071721 | -0.092343 | -0.051494 | -0.048814
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.52067 | 6.3582 | 228.672 | 0.07 | 859 | 2194 | 2445 | 2606 | -0.073355 | -0.091135 | -0.05159 | -0.048558
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.03 | 1378 | 4943 | 5687 | 6061 | -0.0581 | -0.11305 | -0.051376 | -0.048509
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.035 | 1289 | 4261 | 4874 | 5196 | -0.060496 | -0.10876 | -0.051566 | -0.048352
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.04 | 1209 | 3747 | 4265 | 4546 | -0.062791 | -0.10509 | -0.051379 | -0.048556
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.045 | 1136 | 3345 | 3791 | 4041 | -0.06425 | -0.10177 | -0.051539 | -0.048505
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.05 | 1069 | 3022 | 3412 | 3637 | -0.066376 | -0.098986 | -0.051432 | -0.048404
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.055 | 1008 | 2755 | 3102 | 3306 | -0.068392 | -0.096721 | -0.051376 | -0.048633
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.06 | 952 | 2532 | 2843 | 3031 | -0.070312 | -0.094744 | -0.051701 | -0.048352
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.065 | 901 | 2343 | 2625 | 2798 | -0.072091 | -0.093266 | -0.051319 | -0.048299
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.52466 | 6.3826 | 228.672 | 0.07 | 855 | 2179 | 2437 | 2598 | -0.072668 | -0.091705 | -0.051382 | -0.048352
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.03 | 1316 | 4803 | 5423 | 5775 | -0.058655 | -0.10824 | -0.051757 | -0.048913
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.035 | 1232 | 4135 | 4648 | 4950 | -0.060976 | -0.1044 | -0.051816 | -0.048809
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.04 | 1156 | 3632 | 4067 | 4332 | -0.063209 | -0.10099 | -0.05176 | -0.048748
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.045 | 1087 | 3239 | 3615 | 3850 | -0.065348 | -0.098023 | -0.051679 | -0.048913
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.05 | 1023 | 2923 | 3254 | 3465 | -0.067457 | -0.095606 | -0.051588 | -0.048861
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.055 | 966 | 2664 | 2958 | 3150 | -0.068467 | -0.093261 | -0.051619 | -0.048913
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.06 | 913 | 2447 | 2711 | 2888 | -0.070265 | -0.091348 | -0.051766 | -0.048748
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.065 | 864 | 2262 | 2503 | 2666 | -0.072961 | -0.090105 | -0.051535 | -0.048537
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.54709 | 6.3009 | 243.072 | 0.07 | 820 | 2104 | 2324 | 2475 | -0.073446 | -0.088388 | -0.051816 | -0.048809
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.03 | 1156 | 3445 | 4815 | 5173 | -0.058632 | -0.15873 | -0.055512 | -0.050651
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.035 | 1076 | 3015 | 4128 | 4434 | -0.061901 | -0.15094 | -0.055161 | -0.050739
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.04 | 1004 | 2685 | 3613 | 3880 | -0.064306 | -0.14463 | -0.054931 | -0.050648
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.045 | 939 | 2422 | 3211 | 3448 | -0.0666 | -0.139 | -0.055032 | -0.050922
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.05 | 880 | 2207 | 2890 | 3104 | -0.068783 | -0.13451 | -0.055247 | -0.050474
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.055 | 827 | 2028 | 2628 | 2821 | -0.069741 | -0.13073 | -0.054676 | -0.050808
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.06 | 779 | 1875 | 2409 | 2586 | -0.071514 | -0.1275 | -0.054923 | -0.051009
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.065 | 735 | 1744 | 2224 | 2387 | -0.07314 | -0.1245 | -0.054824 | -0.050895
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.55481 | 7.0131 | 243.072 | 0.07 | 695 | 1630 | 2065 | 2217 | -0.074567 | -0.12224 | -0.05492 | -0.050535
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.03 | 1144 | 3331 | 4722 | 5126 | -0.058436 | -0.16328 | -0.064395 | -0.050565
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.035 | 1064 | 2921 | 4053 | 4394 | -0.061728 | -0.15505 | -0.063107 | -0.050562
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.04 | 992 | 2605 | 3550 | 3845 | -0.064151 | -0.14841 | -0.062335 | -0.050383
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.045 | 928 | 2353 | 3158 | 3417 | -0.065458 | -0.14249 | -0.061516 | -0.05057
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.05 | 869 | 2147 | 2845 | 3076 | -0.068596 | -0.13775 | -0.060436 | -0.050324
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.055 | 817 | 1974 | 2588 | 2796 | -0.069476 | -0.13383 | -0.059935 | -0.050594
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.06 | 769 | 1827 | 2374 | 2563 | -0.071256 | -0.13041 | -0.059429 | -0.050389
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.065 | 725 | 1700 | 2192 | 2366 | -0.07289 | -0.12731 | -0.059227 | -0.050562
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.56436 | 7.0732 | 243.072 | 0.07 | 685 | 1590 | 2036 | 2197 | -0.074324 | -0.12493 | -0.058715 | -0.050562
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.03 | 1130 | 3197 | 4615 | 5072 | -0.056761 | -0.16484 | -0.073665 | -0.048941
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.035 | 1050 | 2810 | 3966 | 4348 | -0.059982 | -0.15641 | -0.071194 | -0.048786
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.04 | 979 | 2512 | 3478 | 3804 | -0.061361 | -0.14905 | -0.069058 | -0.049
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.045 | 915 | 2272 | 3097 | 3382 | -0.06346 | -0.14329 | -0.06745 | -0.048664
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.05 | 857 | 2076 | 2791 | 3043 | -0.065431 | -0.13823 | -0.066243 | -0.049063
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.055 | 805 | 1912 | 2542 | 2767 | -0.067207 | -0.13367 | -0.064409 | -0.048814
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.06 | 757 | 1771 | 2332 | 2536 | -0.068881 | -0.13016 | -0.06383 | -0.048762
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.065 | 714 | 1649 | 2155 | 2341 | -0.070312 | -0.12751 | -0.062636 | -0.048761
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.57544 | 7.1423 | 243.072 | 0.07 | 675 | 1543 | 2003 | 2174 | -0.071527 | -0.12479 | -0.061827 | -0.048578
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.03 | 1112 | 3025 | 4477 | 5005 | -0.054422 | -0.16827 | -0.086513 | -0.04703
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.035 | 1033 | 2668 | 3854 | 4290 | -0.057482 | -0.15916 | -0.082599 | -0.04709
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.04 | 963 | 2392 | 3385 | 3753 | -0.058651 | -0.15147 | -0.079162 | -0.04722
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.045 | 899 | 2169 | 3017 | 3336 | -0.061587 | -0.14505 | -0.076523 | -0.047129
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.05 | 842 | 1986 | 2723 | 3003 | -0.062361 | -0.13951 | -0.074124 | -0.046969
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.055 | 790 | 1831 | 2481 | 2730 | -0.065089 | -0.13551 | -0.071829 | -0.04712
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.06 | 743 | 1698 | 2279 | 2502 | -0.066583 | -0.1319 | -0.070175 | -0.04722
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.065 | 700 | 1584 | 2107 | 2310 | -0.067909 | -0.12823 | -0.068523 | -0.04703
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.58934 | 7.228 | 243.072 | 0.07 | 662 | 1483 | 1959 | 2145 | -0.067606 | -0.1261 | -0.067587 | -0.04709
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.03 | 1050 | 2856 | 4226 | 4725 | -0.044586 | -0.14105 | -0.077695 | -0.038266
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.035 | 976 | 2520 | 3639 | 4050 | -0.045943 | -0.13313 | -0.073574 | -0.038233
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.04 | 909 | 2258 | 3195 | 3544 | -0.048168 | -0.12684 | -0.07041 | -0.038263
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.045 | 849 | 2048 | 2849 | 3150 | -0.049272 | -0.12141 | -0.06743 | -0.038168
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.05 | 795 | 1874 | 2571 | 2835 | -0.051313 | -0.11687 | -0.064751 | -0.038331
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.055 | 746 | 1728 | 2342 | 2577 | -0.052097 | -0.11294 | -0.062825 | -0.038433
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.06 | 701 | 1603 | 2151 | 2362 | -0.053981 | -0.10994 | -0.061109 | -0.038665
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.065 | 661 | 1496 | 1990 | 2181 | -0.055714 | -0.10687 | -0.059102 | -0.03836
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.63578 | 7.2281 | 257.472 | 0.07 | 625 | 1400 | 1849 | 2025 | -0.055891 | -0.10486 | -0.058554 | -0.038462
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.03 | 905 | 1438 | 2921 | 4068 | -0.037234 | -0.13634 | -0.10673 | -0.051748
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.035 | 835 | 1345 | 2580 | 3497 | -0.039125 | -0.12492 | -0.098532 | -0.048953
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.04 | 773 | 1262 | 2314 | 3067 | -0.040943 | -0.11563 | -0.092193 | -0.046924
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.045 | 718 | 1186 | 2100 | 2732 | -0.042667 | -0.10894 | -0.086957 | -0.044755
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.05 | 669 | 1116 | 1924 | 2463 | -0.042918 | -0.10433 | -0.082499 | -0.043124
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.055 | 625 | 1053 | 1775 | 2243 | -0.044343 | -0.1 | -0.078401 | -0.041453
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.06 | 585 | 995 | 1648 | 2059 | -0.045677 | -0.097096 | -0.075196 | -0.040093
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.065 | 549 | 942 | 1538 | 1902 | -0.046875 | -0.095101 | -0.072376 | -0.039394
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.65828 | 8.1291 | 257.472 | 0.07 | 517 | 893 | 1440 | 1768 | -0.047882 | -0.09248 | -0.070368 | -0.038608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.03 | 896 | 1425 | 2835 | 3997 | -0.034483 | -0.0625 | -0.10114 | -0.057534
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.035 | 827 | 1333 | 2510 | 3441 | -0.036131 | -0.059944 | -0.093208 | -0.05337
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.04 | 765 | 1250 | 2256 | 3021 | -0.037736 | -0.058026 | -0.087009 | -0.050299
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.045 | 710 | 1174 | 2051 | 2693 | -0.039242 | -0.057028 | -0.081505 | -0.047737
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.05 | 661 | 1105 | 1881 | 2431 | -0.040639 | -0.055556 | -0.077489 | -0.044794
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.055 | 618 | 1042 | 1737 | 2215 | -0.040373 | -0.054446 | -0.074094 | -0.042369
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.06 | 578 | 984 | 1614 | 2035 | -0.043046 | -0.054755 | -0.070812 | -0.040547
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.065 | 543 | 931 | 1508 | 1881 | -0.042328 | -0.055781 | -0.067985 | -0.039326
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.66806 | 8.1892 | 257.472 | 0.07 | 511 | 883 | 1413 | 1749 | -0.043071 | -0.054604 | -0.066094 | -0.037954
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.03 | 893 | 1421 | 2805 | 3973 | -0.034595 | -0.042453 | -0.10211 | -0.060534
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.035 | 824 | 1329 | 2486 | 3422 | -0.036257 | -0.042507 | -0.094353 | -0.056
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.04 | 762 | 1246 | 2236 | 3006 | -0.037879 | -0.043011 | -0.087719 | -0.052333
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.045 | 708 | 1170 | 2034 | 2681 | -0.038043 | -0.043336 | -0.082544 | -0.049291
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.05 | 659 | 1101 | 1867 | 2420 | -0.039359 | -0.04344 | -0.078025 | -0.046493
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.055 | 615 | 1038 | 1725 | 2206 | -0.040562 | -0.043318 | -0.074074 | -0.04378
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.06 | 576 | 980 | 1603 | 2027 | -0.041597 | -0.044834 | -0.071263 | -0.041608
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.065 | 541 | 928 | 1498 | 1874 | -0.042478 | -0.045267 | -0.068408 | -0.039959
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.67105 | 8.2075 | 257.472 | 0.07 | 509 | 880 | 1404 | 1743 | -0.043233 | -0.044517 | -0.066489 | -0.03861
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.03 | 891 | 1417 | 2776 | 3949 | -0.033623 | -0.032104 | -0.10336 | -0.062218
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.035 | 821 | 1325 | 2463 | 3403 | -0.036385 | -0.033552 | -0.094818 | -0.057602
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.04 | 760 | 1242 | 2216 | 2990 | -0.036755 | -0.034215 | -0.088816 | -0.053498
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.045 | 705 | 1166 | 2017 | 2668 | -0.03951 | -0.036364 | -0.083182 | -0.050196
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.05 | 657 | 1097 | 1852 | 2409 | -0.039474 | -0.036874 | -0.078607 | -0.04745
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.055 | 613 | 1034 | 1712 | 2197 | -0.040689 | -0.03814 | -0.075095 | -0.044367
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.06 | 574 | 977 | 1592 | 2018 | -0.041736 | -0.039331 | -0.07172 | -0.042694
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.065 | 539 | 924 | 1488 | 1866 | -0.042629 | -0.040498 | -0.068836 | -0.040617
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.6746 | 8.2292 | 257.472 | 0.07 | 507 | 876 | 1395 | 1736 | -0.043396 | -0.040526 | -0.06689 | -0.039292
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.03 | 876 | 1405 | 2959 | 4005 | -0.035242 | -0.21112 | -0.09261 | -0.031205
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.035 | 809 | 1314 | 2599 | 3433 | -0.036905 | -0.19089 | -0.086146 | -0.031047
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.04 | 750 | 1232 | 2321 | 3004 | -0.038462 | -0.17537 | -0.080792 | -0.030968
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.045 | 697 | 1157 | 2099 | 2670 | -0.039945 | -0.16402 | -0.076551 | -0.031205
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.05 | 650 | 1090 | 1917 | 2403 | -0.039882 | -0.15373 | -0.072569 | -0.031048
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.055 | 608 | 1028 | 1765 | 2185 | -0.041009 | -0.14618 | -0.069093 | -0.031042
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.06 | 569 | 972 | 1635 | 2003 | -0.043697 | -0.13982 | -0.066248 | -0.030963
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.065 | 535 | 920 | 1523 | 1849 | -0.042934 | -0.13452 | -0.063921 | -0.030922
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.69087 | 7.9889 | 271.872 | 0.07 | 504 | 873 | 1425 | 1717 | -0.043643 | -0.13048 | -0.0625 | -0.031038
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.03 | 765 | 1224 | 1751 | 3020 | -0.035309 | -0.033175 | -0.15817 | -0.082067
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.035 | 702 | 1141 | 1619 | 2650 | -0.037037 | -0.03387 | -0.14157 | -0.075044
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.04 | 647 | 1065 | 1506 | 2366 | -0.038633 | -0.036199 | -0.12847 | -0.068871
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.045 | 598 | 996 | 1406 | 2139 | -0.040128 | -0.037681 | -0.1185 | -0.063485
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.05 | 555 | 935 | 1318 | 1953 | -0.041451 | -0.038066 | -0.11066 | -0.059249
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.055 | 517 | 879 | 1240 | 1797 | -0.040816 | -0.039344 | -0.1034 | -0.055702
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.06 | 483 | 828 | 1169 | 1665 | -0.041667 | -0.039443 | -0.097994 | -0.052362
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.065 | 452 | 781 | 1105 | 1550 | -0.044397 | -0.041718 | -0.093519 | -0.050245
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.69697 | 8.8687 | 271.872 | 0.07 | 425 | 739 | 1046 | 1450 | -0.042793 | -0.041505 | -0.089643 | -0.047932
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.03 | 759 | 1216 | 1682 | 2963 | -0.035578 | -0.032617 | -0.16402 | -0.083797
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.035 | 696 | 1132 | 1563 | 2606 | -0.037344 | -0.034953 | -0.1459 | -0.075887
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.04 | 642 | 1057 | 1459 | 2329 | -0.037481 | -0.035584 | -0.13258 | -0.069888
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.045 | 593 | 989 | 1367 | 2108 | -0.040453 | -0.037001 | -0.12147 | -0.064774
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.05 | 550 | 927 | 1284 | 1927 | -0.041812 | -0.038382 | -0.11326 | -0.06
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.055 | 512 | 871 | 1210 | 1775 | -0.042991 | -0.039691 | -0.10569 | -0.056353
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.06 | 478 | 821 | 1142 | 1645 | -0.044 | -0.039766 | -0.10008 | -0.05351
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.065 | 448 | 774 | 1081 | 1533 | -0.042735 | -0.040892 | -0.095397 | -0.050774
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.70466 | 8.9175 | 271.872 | 0.07 | 421 | 732 | 1024 | 1435 | -0.043182 | -0.041885 | -0.092199 | -0.048408
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.03 | 753 | 1208 | 1613 | 2907 | -0.032134 | -0.029719 | -0.1577 | -0.078605
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.035 | 691 | 1124 | 1507 | 2561 | -0.033566 | -0.031869 | -0.13984 | -0.071429
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.04 | 636 | 1049 | 1413 | 2293 | -0.036364 | -0.032288 | -0.12616 | -0.065226
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.045 | 588 | 981 | 1328 | 2078 | -0.036066 | -0.033498 | -0.11526 | -0.060579
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.05 | 546 | 920 | 1250 | 1901 | -0.037037 | -0.034627 | -0.10714 | -0.056107
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.055 | 508 | 864 | 1180 | 1753 | -0.037879 | -0.035714 | -0.099924 | -0.052432
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.06 | 474 | 814 | 1116 | 1626 | -0.03854 | -0.036686 | -0.094156 | -0.049679
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.065 | 444 | 768 | 1057 | 1516 | -0.038961 | -0.037594 | -0.090361 | -0.04714
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.71349 | 8.9732 | 271.872 | 0.07 | 417 | 726 | 1003 | 1420 | -0.039171 | -0.038411 | -0.086521 | -0.045057
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.03 | 746 | 1196 | 1563 | 2828 | -0.029909 | -0.028432 | -0.13407 | -0.077325
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.035 | 684 | 1113 | 1466 | 2498 | -0.031161 | -0.029643 | -0.11846 | -0.069993
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.04 | 629 | 1038 | 1378 | 2242 | -0.033794 | -0.030812 | -0.10693 | -0.063883
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.045 | 581 | 971 | 1297 | 2036 | -0.034884 | -0.031904 | -0.098053 | -0.058715
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.05 | 539 | 910 | 1223 | 1865 | -0.035778 | -0.032944 | -0.091382 | -0.054739
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.055 | 502 | 854 | 1155 | 1722 | -0.034615 | -0.033937 | -0.085511 | -0.05124
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.06 | 468 | 804 | 1093 | 1599 | -0.037037 | -0.034814 | -0.081513 | -0.048214
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.065 | 438 | 759 | 1036 | 1492 | -0.037363 | -0.035578 | -0.078292 | -0.046036
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.72443 | 9.0417 | 271.872 | 0.07 | 412 | 717 | 983 | 1399 | -0.037383 | -0.03629 | -0.075259 | -0.043746

## 25%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | % change from normal
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | Very Slow | Slow | Moderate | Fast
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.03 | 2629 | 9738 | 10172 | 10625 | -0.027377 | -0.023466 | -0.022393 | -0.021369
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.035 | 2505 | 8347 | 8719 | 9108 | -0.028317 | -0.023514 | -0.022424 | -0.021277
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.04 | 2389 | 7304 | 7629 | 7969 | -0.029651 | -0.023399 | -0.022424 | -0.021368
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.045 | 2281 | 6492 | 6781 | 7084 | -0.030187 | -0.023466 | -0.022488 | -0.021277
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.05 | 2179 | 5843 | 6103 | 6375 | -0.031556 | -0.0234 | -0.022425 | -0.021339
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.055 | 2085 | 5312 | 5548 | 5796 | -0.032033 | -0.023529 | -0.022551 | -0.021277
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.06 | 1996 | 4869 | 5086 | 5313 | -0.032946 | -0.023466 | -0.022487 | -0.021367
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.065 | 1912 | 4495 | 4695 | 4904 | -0.033855 | -0.023463 | -0.022486 | -0.021353
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.4746 | 4.3637 | 185.472 | 0.07 | 1834 | 4174 | 4359 | 4554 | -0.034737 | -0.023397 | -0.022427 | -0.021277
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.03 | 2353 | 8845 | 9282 | 9741 | -0.027686 | -0.024377 | -0.023153 | -0.02189
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.035 | 2232 | 7582 | 7956 | 8349 | -0.028721 | -0.024321 | -0.023204 | -0.022022
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.04 | 2120 | 6634 | 6962 | 7305 | -0.029748 | -0.024268 | -0.023151 | -0.021957
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.045 | 2016 | 5897 | 6188 | 6494 | -0.030769 | -0.024322 | -0.023204 | -0.021988
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.05 | 1919 | 5307 | 5569 | 5844 | -0.031786 | -0.024269 | -0.023154 | -0.022088
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.055 | 1829 | 4825 | 5063 | 5313 | -0.032787 | -0.024267 | -0.023153 | -0.021907
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.06 | 1745 | 4423 | 4641 | 4870 | -0.033776 | -0.024266 | -0.023153 | -0.022088
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.065 | 1667 | 4083 | 4284 | 4496 | -0.034183 | -0.02414 | -0.023256 | -0.021971
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47413 | 4.8207 | 185.472 | 0.07 | 1594 | 3791 | 3978 | 4175 | -0.035109 | -0.024196 | -0.023084 | -0.02179
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.03 | 2353 | 8845 | 9282 | 9741 | -0.030091 | -0.026417 | -0.025102 | -0.023752
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.035 | 2232 | 7582 | 7956 | 8349 | -0.03125 | -0.026326 | -0.025119 | -0.023737
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.04 | 2120 | 6634 | 6962 | 7305 | -0.032405 | -0.026273 | -0.025067 | -0.023787
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.045 | 2016 | 5897 | 6188 | 6494 | -0.033557 | -0.026255 | -0.025051 | -0.023752
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.05 | 1919 | 5307 | 5569 | 5844 | -0.034708 | -0.026417 | -0.025035 | -0.023885
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.055 | 1829 | 4825 | 5063 | 5313 | -0.035338 | -0.026236 | -0.025034 | -0.023705
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.06 | 1745 | 4423 | 4641 | 4870 | -0.036444 | -0.0262 | -0.025 | -0.023852
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.065 | 1667 | 4083 | 4284 | 4496 | -0.036973 | -0.026234 | -0.025034 | -0.02367
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.47384 | 4.8192 | 185.472 | 0.07 | 1594 | 3791 | 3978 | 4175 | -0.038021 | -0.026201 | -0.025 | -0.02362
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.03 | 2353 | 8845 | 9282 | 9741 | -0.030091 | -0.026417 | -0.025102 | -0.023752
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.035 | 2232 | 7582 | 7956 | 8349 | -0.03125 | -0.026326 | -0.025119 | -0.023737
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.04 | 2120 | 6634 | 6962 | 7305 | -0.032405 | -0.026273 | -0.025067 | -0.023787
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.045 | 2016 | 5897 | 6188 | 6494 | -0.033557 | -0.026255 | -0.025051 | -0.023752
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.05 | 1919 | 5307 | 5569 | 5844 | -0.034708 | -0.026417 | -0.025035 | -0.023885
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.055 | 1829 | 4825 | 5063 | 5313 | -0.035338 | -0.026236 | -0.025034 | -0.023705
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.06 | 1745 | 4423 | 4641 | 4870 | -0.036444 | -0.0262 | -0.025 | -0.023852
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.065 | 1667 | 4083 | 4284 | 4496 | -0.036973 | -0.026234 | -0.025034 | -0.02367
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.4735 | 4.8175 | 185.472 | 0.07 | 1594 | 3791 | 3978 | 4175 | -0.038021 | -0.026201 | -0.025 | -0.02362
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.03 | 2353 | 8845 | 9282 | 9741 | -0.030091 | -0.026417 | -0.025102 | -0.023752
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.035 | 2232 | 7582 | 7956 | 8349 | -0.03125 | -0.026326 | -0.025119 | -0.023737
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.04 | 2120 | 6634 | 6962 | 7305 | -0.032405 | -0.026273 | -0.025067 | -0.023787
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.045 | 2016 | 5897 | 6188 | 6494 | -0.033557 | -0.026255 | -0.025051 | -0.023752
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.05 | 1919 | 5307 | 5569 | 5844 | -0.034708 | -0.026417 | -0.025035 | -0.023885
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.055 | 1829 | 4825 | 5063 | 5313 | -0.035338 | -0.026236 | -0.025034 | -0.023705
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.06 | 1745 | 4423 | 4641 | 4870 | -0.036444 | -0.0262 | -0.025 | -0.023852
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.065 | 1667 | 4083 | 4284 | 4496 | -0.036973 | -0.026234 | -0.025034 | -0.02367
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.47317 | 4.8158 | 185.472 | 0.07 | 1594 | 3791 | 3978 | 4175 | -0.038021 | -0.026201 | -0.025 | -0.02362
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.03 | 2230 | 8361 | 8766 | 9190 | -0.027899 | -0.024501 | -0.023396 | -0.022236
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.035 | 2117 | 7166 | 7514 | 7878 | -0.029344 | -0.024636 | -0.023268 | -0.022095
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.04 | 2012 | 6271 | 6574 | 6893 | -0.030361 | -0.024424 | -0.02347 | -0.022131
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.045 | 1915 | 5574 | 5844 | 6127 | -0.031361 | -0.024501 | -0.023396 | -0.022183
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.05 | 1824 | 5017 | 5260 | 5514 | -0.032361 | -0.024499 | -0.023213 | -0.022167
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.055 | 1740 | 4560 | 4781 | 5013 | -0.033333 | -0.024599 | -0.023489 | -0.022235
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.06 | 1661 | 4180 | 4383 | 4595 | -0.034302 | -0.024732 | -0.023396 | -0.02234
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.065 | 1588 | 3859 | 4046 | 4242 | -0.03465 | -0.02452 | -0.023413 | -0.02213
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.47262 | 4.7299 | 199.872 | 0.07 | 1519 | 3583 | 3757 | 3939 | -0.035556 | -0.024503 | -0.023395 | -0.022095
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.03 | 1991 | 7563 | 7969 | 8397 | -0.0302 | -0.027267 | -0.025914 | -0.024512
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.035 | 1881 | 6483 | 6831 | 7198 | -0.031909 | -0.027161 | -0.025813 | -0.024397
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.04 | 1781 | 5673 | 5977 | 6298 | -0.032591 | -0.027097 | -0.025913 | -0.024473
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.045 | 1687 | 5042 | 5313 | 5598 | -0.034345 | -0.027204 | -0.025853 | -0.024569
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.05 | 1601 | 4538 | 4782 | 5038 | -0.034961 | -0.027224 | -0.025672 | -0.024589
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.055 | 1522 | 4125 | 4347 | 4580 | -0.035488 | -0.027352 | -0.025773 | -0.024494
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.06 | 1448 | 3782 | 3985 | 4199 | -0.036593 | -0.027013 | -0.025672 | -0.024396
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.065 | 1379 | 3491 | 3678 | 3876 | -0.037683 | -0.027035 | -0.025953 | -0.024415
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.47263 | 5.2279 | 199.872 | 0.07 | 1316 | 3241 | 3415 | 3599 | -0.038012 | -0.027311 | -0.025956 | -0.024397
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.03 | 1991 | 7563 | 7969 | 8397 | -0.0302 | -0.027267 | -0.025914 | -0.024512
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.035 | 1881 | 6483 | 6831 | 7198 | -0.031909 | -0.027161 | -0.025813 | -0.024397
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.04 | 1781 | 5673 | 5977 | 6298 | -0.032591 | -0.027097 | -0.025913 | -0.024473
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.045 | 1687 | 5042 | 5313 | 5598 | -0.034345 | -0.027204 | -0.025853 | -0.024569
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.05 | 1601 | 4538 | 4782 | 5038 | -0.034961 | -0.027224 | -0.025672 | -0.024589
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.055 | 1522 | 4125 | 4347 | 4580 | -0.035488 | -0.027352 | -0.025773 | -0.024494
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.06 | 1448 | 3782 | 3985 | 4199 | -0.036593 | -0.027013 | -0.025672 | -0.024396
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.065 | 1379 | 3491 | 3678 | 3876 | -0.037683 | -0.027035 | -0.025953 | -0.024415
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.47289 | 5.2293 | 199.872 | 0.07 | 1316 | 3241 | 3415 | 3599 | -0.038012 | -0.027311 | -0.025956 | -0.024397
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.03 | 1991 | 7563 | 7969 | 8397 | -0.028306 | -0.025261 | -0.024005 | -0.022809
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.035 | 1881 | 6483 | 6831 | 7198 | -0.029912 | -0.025259 | -0.024003 | -0.022675
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.04 | 1781 | 5673 | 5977 | 6298 | -0.030484 | -0.025258 | -0.024004 | -0.022657
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.045 | 1687 | 5042 | 5313 | 5598 | -0.031573 | -0.025324 | -0.024063 | -0.022696
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.05 | 1601 | 4538 | 4782 | 5038 | -0.032628 | -0.025344 | -0.023882 | -0.022886
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.055 | 1522 | 4125 | 4347 | 4580 | -0.033037 | -0.025284 | -0.024023 | -0.022829
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.06 | 1448 | 3782 | 3985 | 4199 | -0.034023 | -0.025258 | -0.024002 | -0.022579
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.065 | 1379 | 3491 | 3678 | 3876 | -0.03499 | -0.025133 | -0.024144 | -0.022693
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.47285 | 5.2291 | 199.872 | 0.07 | 1316 | 3241 | 3415 | 3599 | -0.035191 | -0.025263 | -0.024007 | -0.022807
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.03 | 1991 | 7563 | 7969 | 8397 | -0.028306 | -0.025261 | -0.024005 | -0.022809
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.035 | 1881 | 6483 | 6831 | 7198 | -0.029912 | -0.025259 | -0.024003 | -0.022675
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.04 | 1781 | 5673 | 5977 | 6298 | -0.030484 | -0.025258 | -0.024004 | -0.022657
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.045 | 1687 | 5042 | 5313 | 5598 | -0.031573 | -0.025324 | -0.024063 | -0.022696
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.05 | 1601 | 4538 | 4782 | 5038 | -0.032628 | -0.025344 | -0.023882 | -0.022886
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.055 | 1522 | 4125 | 4347 | 4580 | -0.033037 | -0.025284 | -0.024023 | -0.022829
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.06 | 1448 | 3782 | 3985 | 4199 | -0.034023 | -0.025258 | -0.024002 | -0.022579
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.065 | 1379 | 3491 | 3678 | 3876 | -0.03499 | -0.025133 | -0.024144 | -0.022693
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.4729 | 5.2294 | 199.872 | 0.07 | 1316 | 3241 | 3415 | 3599 | -0.035191 | -0.025263 | -0.024007 | -0.022807
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.03 | 1903 | 7209 | 7588 | 7987 | -0.028586 | -0.025547 | -0.024302 | -0.022997
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.035 | 1800 | 6180 | 6504 | 6846 | -0.02965 | -0.02539 | -0.024302 | -0.022977
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.04 | 1705 | 5407 | 5691 | 5990 | -0.03125 | -0.02559 | -0.024344 | -0.022998
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.045 | 1617 | 4806 | 5059 | 5325 | -0.032316 | -0.025547 | -0.024301 | -0.022936
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.05 | 1536 | 4326 | 4553 | 4792 | -0.032746 | -0.025456 | -0.024218 | -0.023038
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.055 | 1461 | 3932 | 4139 | 4356 | -0.03373 | -0.025527 | -0.024281 | -0.023099
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.06 | 1391 | 3605 | 3794 | 3993 | -0.034698 | -0.025412 | -0.024177 | -0.023
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.065 | 1326 | 3327 | 3502 | 3686 | -0.035636 | -0.025769 | -0.024241 | -0.023059
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.47542 | 5.1205 | 214.272 | 0.07 | 1266 | 3090 | 3252 | 3423 | -0.035796 | -0.025544 | -0.024302 | -0.022838
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.03 | 1695 | 6496 | 6875 | 7275 | -0.028653 | -0.026233 | -0.024823 | -0.02349
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.035 | 1596 | 5568 | 5893 | 6236 | -0.029787 | -0.026233 | -0.024822 | -0.023336
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.04 | 1505 | 4872 | 5156 | 5456 | -0.030908 | -0.026184 | -0.024778 | -0.023447
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.045 | 1421 | 4331 | 4583 | 4850 | -0.032016 | -0.026085 | -0.024894 | -0.023359
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.05 | 1344 | 3898 | 4125 | 4365 | -0.033094 | -0.02623 | -0.024823 | -0.02349
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.055 | 1274 | 3544 | 3750 | 3968 | -0.034117 | -0.026106 | -0.024707 | -0.023382
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.06 | 1209 | 3248 | 3437 | 3638 | -0.034345 | -0.026379 | -0.024965 | -0.023356
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.065 | 1148 | 2998 | 3173 | 3358 | -0.036104 | -0.026307 | -0.024892 | -0.023269
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.47611 | 5.6635 | 214.272 | 0.07 | 1093 | 2784 | 2946 | 3118 | -0.036155 | -0.026233 | -0.024826 | -0.023489
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.03 | 1692 | 6484 | 6863 | 7263 | -0.030372 | -0.028032 | -0.026525 | -0.025101
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.035 | 1592 | 5558 | 5882 | 6225 | -0.032219 | -0.027982 | -0.026642 | -0.025059
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.04 | 1502 | 4863 | 5147 | 5447 | -0.03284 | -0.027983 | -0.02648 | -0.025058
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.045 | 1418 | 4323 | 4575 | 4842 | -0.03406 | -0.027884 | -0.026596 | -0.02497
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.05 | 1341 | 3891 | 4118 | 4358 | -0.035252 | -0.027979 | -0.026478 | -0.025056
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.055 | 1271 | 3537 | 3743 | 3962 | -0.036391 | -0.02803 | -0.026528 | -0.024858
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.06 | 1205 | 3242 | 3431 | 3631 | -0.03754 | -0.028177 | -0.026667 | -0.025235
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.065 | 1145 | 2993 | 3167 | 3352 | -0.038623 | -0.027931 | -0.026736 | -0.025015
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.47688 | 5.6681 | 214.272 | 0.07 | 1090 | 2779 | 2941 | 3113 | -0.038801 | -0.027982 | -0.026481 | -0.025055
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.03 | 1692 | 6484 | 6863 | 7263 | -0.028703 | -0.026134 | -0.024726 | -0.023397
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.035 | 1592 | 5558 | 5882 | 6225 | -0.02986 | -0.026108 | -0.024867 | -0.023529
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.04 | 1502 | 4863 | 5147 | 5447 | -0.030968 | -0.026231 | -0.02482 | -0.023485
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.045 | 1418 | 4323 | 4575 | 4842 | -0.032082 | -0.026132 | -0.024728 | -0.023397
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.05 | 1341 | 3891 | 4118 | 4358 | -0.033165 | -0.026033 | -0.024633 | -0.023308
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.055 | 1271 | 3537 | 3743 | 3962 | -0.03346 | -0.026156 | -0.024752 | -0.023416
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.06 | 1205 | 3242 | 3431 | 3631 | -0.035228 | -0.026134 | -0.02473 | -0.023662
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.065 | 1145 | 2993 | 3167 | 3352 | -0.036195 | -0.026033 | -0.024938 | -0.02331
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.47781 | 5.6737 | 214.272 | 0.07 | 1090 | 2779 | 2941 | 3113 | -0.036251 | -0.026279 | -0.024867 | -0.023219
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.03 | 1688 | 6472 | 6850 | 7251 | -0.030999 | -0.027936 | -0.026574 | -0.02501
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.035 | 1589 | 5547 | 5872 | 6215 | -0.031688 | -0.028036 | -0.026525 | -0.025098
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.04 | 1498 | 4854 | 5138 | 5438 | -0.033548 | -0.028034 | -0.026525 | -0.025099
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.045 | 1415 | 4315 | 4567 | 4834 | -0.03413 | -0.027934 | -0.026434 | -0.02501
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.05 | 1338 | 3883 | 4110 | 4350 | -0.035328 | -0.028035 | -0.026528 | -0.025101
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.055 | 1268 | 3530 | 3737 | 3955 | -0.035741 | -0.028084 | -0.026316 | -0.025142
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.06 | 1202 | 3236 | 3425 | 3625 | -0.03763 | -0.027936 | -0.026435 | -0.025276
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.065 | 1142 | 2987 | 3162 | 3346 | -0.038721 | -0.027986 | -0.026478 | -0.025058
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.47903 | 5.6809 | 214.272 | 0.07 | 1087 | 2774 | 2936 | 3107 | -0.038904 | -0.028031 | -0.026525 | -0.025102
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.03 | 1618 | 6192 | 6547 | 6922 | -0.031138 | -0.028249 | -0.026758 | -0.025208
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.035 | 1525 | 5307 | 5611 | 5933 | -0.03236 | -0.028378 | -0.026882 | -0.0253
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.04 | 1439 | 4644 | 4910 | 5191 | -0.03358 | -0.028249 | -0.026759 | -0.025347
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.045 | 1360 | 4128 | 4364 | 4614 | -0.034776 | -0.028249 | -0.026762 | -0.025349
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.05 | 1287 | 3715 | 3928 | 4153 | -0.035955 | -0.02825 | -0.026759 | -0.025346
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.055 | 1220 | 3377 | 3571 | 3775 | -0.037096 | -0.028481 | -0.02671 | -0.025303
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.06 | 1158 | 3096 | 3273 | 3461 | -0.038206 | -0.028249 | -0.026762 | -0.025345
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.065 | 1101 | 2858 | 3021 | 3195 | -0.039267 | -0.028222 | -0.027053 | -0.02532
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.48797 | 5.5691 | 228.672 | 0.07 | 1049 | 2654 | 2806 | 2966 | -0.039377 | -0.028195 | -0.026708 | -0.025304
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.03 | 1435 | 5369 | 5893 | 6268 | -0.030405 | -0.057243 | -0.027237 | -0.025649
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.035 | 1345 | 4613 | 5051 | 5373 | -0.031677 | -0.054907 | -0.027157 | -0.025571
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.04 | 1263 | 4045 | 4420 | 4701 | -0.032925 | -0.053137 | -0.027075 | -0.025699
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.045 | 1188 | 3602 | 3929 | 4179 | -0.034146 | -0.051606 | -0.026994 | -0.025647
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.05 | 1120 | 3247 | 3536 | 3761 | -0.035314 | -0.050029 | -0.027235 | -0.025648
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.055 | 1057 | 2955 | 3214 | 3419 | -0.036463 | -0.048922 | -0.02724 | -0.025648
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.06 | 1000 | 2712 | 2947 | 3134 | -0.037536 | -0.047753 | -0.027072 | -0.025498
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.065 | 948 | 2506 | 2720 | 2893 | -0.037563 | -0.047148 | -0.027182 | -0.025598
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.49052 | 6.1714 | 228.672 | 0.07 | 899 | 2328 | 2526 | 2686 | -0.03953 | -0.046683 | -0.026965 | -0.025753
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.03 | 1429 | 5329 | 5873 | 6248 | -0.030529 | -0.057481 | -0.027166 | -0.025577
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.035 | 1339 | 4580 | 5034 | 5355 | -0.032514 | -0.055281 | -0.027058 | -0.025655
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.04 | 1257 | 4017 | 4405 | 4686 | -0.03382 | -0.053264 | -0.027164 | -0.025577
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.045 | 1183 | 3578 | 3915 | 4165 | -0.034286 | -0.051683 | -0.027087 | -0.025731
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.05 | 1115 | 3225 | 3524 | 3749 | -0.035467 | -0.050633 | -0.027057 | -0.025474
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.055 | 1053 | 2936 | 3203 | 3408 | -0.035714 | -0.049223 | -0.027331 | -0.02545
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.06 | 995 | 2695 | 2936 | 3124 | -0.037718 | -0.04804 | -0.02717 | -0.025577
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.065 | 943 | 2491 | 2711 | 2884 | -0.038736 | -0.047419 | -0.02692 | -0.025346
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.49352 | 6.1903 | 228.672 | 0.07 | 895 | 2314 | 2517 | 2678 | -0.038668 | -0.046952 | -0.027058 | -0.025473
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.03 | 1424 | 5288 | 5853 | 6228 | -0.030633 | -0.057901 | -0.027094 | -0.025505
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.035 | 1334 | 4546 | 5017 | 5338 | -0.03193 | -0.055671 | -0.026959 | -0.025557
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.04 | 1252 | 3988 | 4390 | 4671 | -0.033205 | -0.053855 | -0.027039 | -0.025454
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.045 | 1178 | 3553 | 3902 | 4152 | -0.034426 | -0.052281 | -0.027175 | -0.025581
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.05 | 1110 | 3204 | 3512 | 3737 | -0.035621 | -0.050667 | -0.027147 | -0.025554
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.055 | 1048 | 2917 | 3193 | 3397 | -0.035879 | -0.049528 | -0.026821 | -0.025531
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.06 | 991 | 2677 | 2926 | 3114 | -0.036929 | -0.048685 | -0.027261 | -0.025657
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.065 | 939 | 2475 | 2701 | 2874 | -0.03791 | -0.047711 | -0.027368 | -0.025763
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.4967 | 6.2102 | 228.672 | 0.07 | 891 | 2300 | 2508 | 2669 | -0.038835 | -0.047225 | -0.027153 | -0.025557
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.03 | 1418 | 5248 | 5833 | 6208 | -0.030759 | -0.058317 | -0.027023 | -0.025432
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.035 | 1329 | 4513 | 5000 | 5321 | -0.031341 | -0.056055 | -0.027048 | -0.025458
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.04 | 1247 | 3960 | 4375 | 4656 | -0.033333 | -0.054215 | -0.026913 | -0.025534
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.045 | 1173 | 3529 | 3889 | 4139 | -0.033773 | -0.052363 | -0.02702 | -0.02543
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.05 | 1105 | 3182 | 3500 | 3725 | -0.034934 | -0.051282 | -0.026967 | -0.025379
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.055 | 1043 | 2898 | 3182 | 3386 | -0.036044 | -0.049836 | -0.026911 | -0.025612
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.06 | 986 | 2660 | 2917 | 3104 | -0.037109 | -0.048981 | -0.027018 | -0.025432
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.065 | 934 | 2460 | 2692 | 2865 | -0.038105 | -0.047988 | -0.027105 | -0.02551
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.5005 | 6.2339 | 228.672 | 0.07 | 886 | 2286 | 2500 | 2661 | -0.039046 | -0.047103 | -0.026859 | -0.025275
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.03 | 1352 | 5070 | 5554 | 5906 | -0.032904 | -0.058671 | -0.028851 | -0.027339
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.035 | 1268 | 4356 | 4760 | 5063 | -0.033537 | -0.05653 | -0.028968 | -0.027095
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.04 | 1190 | 3819 | 4165 | 4430 | -0.035656 | -0.054703 | -0.028911 | -0.027229
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.045 | 1120 | 3400 | 3702 | 3938 | -0.036973 | -0.053189 | -0.028856 | -0.027174
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.05 | 1056 | 3065 | 3332 | 3544 | -0.037375 | -0.051671 | -0.028855 | -0.027175
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.055 | 997 | 2790 | 3029 | 3222 | -0.038573 | -0.050374 | -0.028855 | -0.027174
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.06 | 943 | 2559 | 2777 | 2953 | -0.039715 | -0.049759 | -0.028681 | -0.027339
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.065 | 894 | 2364 | 2563 | 2726 | -0.040773 | -0.049075 | -0.028799 | -0.027123
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.52222 | 6.156 | 243.072 | 0.07 | 848 | 2197 | 2380 | 2531 | -0.041808 | -0.048094 | -0.028968 | -0.027287
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.03 | 1189 | 3751 | 4949 | 5300 | -0.031759 | -0.084005 | -0.029227 | -0.027344
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.035 | 1108 | 3268 | 4242 | 4543 | -0.034002 | -0.079696 | -0.029068 | -0.027403
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.04 | 1035 | 2899 | 3712 | 3975 | -0.035415 | -0.076457 | -0.029035 | -0.027404
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.045 | 969 | 2606 | 3300 | 3533 | -0.036779 | -0.073587 | -0.02884 | -0.027525
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.05 | 910 | 2369 | 2970 | 3180 | -0.037037 | -0.07098 | -0.029094 | -0.027225
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.055 | 855 | 2171 | 2700 | 2891 | -0.038245 | -0.069438 | -0.028777 | -0.027254
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.06 | 806 | 2004 | 2475 | 2650 | -0.039333 | -0.067473 | -0.029031 | -0.027523
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.065 | 761 | 1861 | 2284 | 2446 | -0.040353 | -0.065763 | -0.029324 | -0.027435
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.52988 | 6.8537 | 243.072 | 0.07 | 720 | 1737 | 2121 | 2272 | -0.041278 | -0.06462 | -0.029291 | -0.026981
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.03 | 1174 | 3617 | 4893 | 5244 | -0.033745 | -0.091434 | -0.030513 | -0.028709
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.035 | 1094 | 3157 | 4194 | 4495 | -0.035273 | -0.08678 | -0.030513 | -0.028738
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.04 | 1021 | 2805 | 3670 | 3933 | -0.036792 | -0.083034 | -0.030639 | -0.028649
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.045 | 956 | 2526 | 3262 | 3496 | -0.037261 | -0.079446 | -0.030609 | -0.028619
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.05 | 897 | 2298 | 2936 | 3146 | -0.038585 | -0.077108 | -0.030383 | -0.028713
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.055 | 843 | 2109 | 2669 | 2860 | -0.039863 | -0.074594 | -0.030512 | -0.028862
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.06 | 794 | 1948 | 2447 | 2622 | -0.041063 | -0.072822 | -0.030507 | -0.028529
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.065 | 749 | 1810 | 2258 | 2420 | -0.042199 | -0.070842 | -0.030901 | -0.028892
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.53949 | 6.9156 | 243.072 | 0.07 | 709 | 1690 | 2097 | 2247 | -0.041892 | -0.069895 | -0.030513 | -0.028954
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.03 | 1160 | 3484 | 4838 | 5188 | -0.03172 | -0.089864 | -0.028904 | -0.027189
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.035 | 1080 | 3047 | 4147 | 4447 | -0.033124 | -0.08526 | -0.028806 | -0.027128
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.04 | 1008 | 2712 | 3629 | 3891 | -0.033557 | -0.081301 | -0.02864 | -0.02725
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.045 | 943 | 2445 | 3225 | 3459 | -0.0348 | -0.078054 | -0.028907 | -0.027004
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.05 | 884 | 2228 | 2903 | 3113 | -0.035987 | -0.075135 | -0.028772 | -0.027187
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.055 | 830 | 2046 | 2639 | 2830 | -0.038239 | -0.07295 | -0.028708 | -0.027157
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.06 | 782 | 1892 | 2419 | 2594 | -0.03813 | -0.070727 | -0.028904 | -0.027007
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.065 | 738 | 1759 | 2233 | 2395 | -0.039062 | -0.069312 | -0.028708 | -0.026818
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.5509 | 6.9883 | 243.072 | 0.07 | 698 | 1643 | 2073 | 2224 | -0.03989 | -0.068066 | -0.02904 | -0.026696
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.03 | 1142 | 3312 | 4707 | 5118 | -0.028912 | -0.089359 | -0.039584 | -0.025514
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.035 | 1062 | 2905 | 4040 | 4387 | -0.031022 | -0.084463 | -0.038324 | -0.025544
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.04 | 990 | 2592 | 3540 | 3839 | -0.032258 | -0.080525 | -0.036997 | -0.025387
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.045 | 926 | 2341 | 3150 | 3412 | -0.033403 | -0.077257 | -0.035813 | -0.025421
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.05 | 868 | 2137 | 2837 | 3071 | -0.033408 | -0.07409 | -0.035362 | -0.025389
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.055 | 815 | 1965 | 2582 | 2792 | -0.035503 | -0.072238 | -0.034044 | -0.02548
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.06 | 767 | 1819 | 2368 | 2559 | -0.036432 | -0.070041 | -0.033864 | -0.025514
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.065 | 723 | 1693 | 2186 | 2362 | -0.037284 | -0.068244 | -0.033599 | -0.025578
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.56552 | 7.0805 | 243.072 | 0.07 | 684 | 1583 | 2031 | 2194 | -0.03662 | -0.067177 | -0.033317 | -0.025322
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.03 | 1072 | 3072 | 4400 | 4810 | -0.024568 | -0.07609 | -0.039721 | -0.020965
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.035 | 997 | 2698 | 3780 | 4123 | -0.025415 | -0.071895 | -0.037678 | -0.020898
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.04 | 930 | 2410 | 3312 | 3608 | -0.026178 | -0.068059 | -0.036369 | -0.020896
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.045 | 869 | 2179 | 2949 | 3207 | -0.026876 | -0.065208 | -0.034697 | -0.020763
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.05 | 814 | 1988 | 2657 | 2886 | -0.02864 | -0.063148 | -0.033467 | -0.021031
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.055 | 765 | 1830 | 2418 | 2624 | -0.027954 | -0.060575 | -0.032413 | -0.020896
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.06 | 719 | 1694 | 2218 | 2405 | -0.02969 | -0.059411 | -0.031864 | -0.021164
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.065 | 679 | 1578 | 2050 | 2220 | -0.03 | -0.05791 | -0.030733 | -0.021164
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.61461 | 7.1067 | 257.472 | 0.07 | 641 | 1476 | 1904 | 2062 | -0.031722 | -0.056266 | -0.03055 | -0.020893
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.03 | 921 | 1461 | 3081 | 4199 | -0.020213 | -0.12252 | -0.057798 | -0.021212
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.035 | 850 | 1369 | 2709 | 3601 | -0.021864 | -0.1093 | -0.053459 | -0.020669
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.04 | 788 | 1284 | 2422 | 3152 | -0.022333 | -0.10021 | -0.049823 | -0.02051
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.045 | 732 | 1208 | 2192 | 2802 | -0.024 | -0.092412 | -0.046957 | -0.02028
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.05 | 682 | 1137 | 2003 | 2523 | -0.02432 | -0.08748 | -0.044826 | -0.019814
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.055 | 638 | 1073 | 1844 | 2295 | -0.024465 | -0.082906 | -0.042575 | -0.019231
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.06 | 598 | 1015 | 1709 | 2104 | -0.02447 | -0.078947 | -0.040965 | -0.019114
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.065 | 562 | 961 | 1593 | 1942 | -0.024306 | -0.076849 | -0.039204 | -0.019192
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.64005 | 8.0157 | 257.472 | 0.07 | 529 | 912 | 1490 | 1804 | -0.025783 | -0.073171 | -0.038089 | -0.019032
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.03 | 912 | 1448 | 2994 | 4128 | -0.017241 | -0.047368 | -0.050729 | -0.026645
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.035 | 842 | 1356 | 2639 | 3544 | -0.018648 | -0.043724 | -0.046604 | -0.025034
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.04 | 780 | 1272 | 2363 | 3105 | -0.018868 | -0.041447 | -0.043707 | -0.023892
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.045 | 724 | 1195 | 2142 | 2764 | -0.020298 | -0.040161 | -0.040752 | -0.022631
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.05 | 675 | 1126 | 1960 | 2491 | -0.020319 | -0.037607 | -0.038744 | -0.021218
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.055 | 631 | 1062 | 1807 | 2267 | -0.020186 | -0.036298 | -0.03678 | -0.019888
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.06 | 591 | 1004 | 1676 | 2079 | -0.021523 | -0.035543 | -0.035118 | -0.019802
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.065 | 555 | 950 | 1563 | 1920 | -0.021164 | -0.036511 | -0.033993 | -0.019408
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.65106 | 8.0844 | 257.472 | 0.07 | 523 | 901 | 1463 | 1784 | -0.020599 | -0.035332 | -0.033047 | -0.018702
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.03 | 909 | 1444 | 2965 | 4104 | -0.017297 | -0.026954 | -0.050896 | -0.029558
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.035 | 839 | 1352 | 2615 | 3526 | -0.018713 | -0.025937 | -0.047359 | -0.02731
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.04 | 777 | 1268 | 2344 | 3090 | -0.018939 | -0.026114 | -0.043656 | -0.025851
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.045 | 722 | 1191 | 2125 | 2751 | -0.019022 | -0.026165 | -0.041498 | -0.024468
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.05 | 672 | 1122 | 1946 | 2480 | -0.020408 | -0.025195 | -0.039012 | -0.022853
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.055 | 628 | 1058 | 1794 | 2257 | -0.020281 | -0.024885 | -0.037037 | -0.021673
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.06 | 588 | 1000 | 1665 | 2071 | -0.021631 | -0.025341 | -0.035342 | -0.020804
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.065 | 553 | 947 | 1553 | 1913 | -0.021239 | -0.02572 | -0.034204 | -0.01998
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.65395 | 8.1023 | 257.472 | 0.07 | 520 | 898 | 1454 | 1778 | -0.022556 | -0.024973 | -0.033245 | -0.019305
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.03 | 906 | 1440 | 2936 | 4080 | -0.017354 | -0.016393 | -0.05168 | -0.031109
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.035 | 836 | 1348 | 2592 | 3507 | -0.018779 | -0.016776 | -0.047409 | -0.028801
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.04 | 774 | 1264 | 2324 | 3075 | -0.019011 | -0.017107 | -0.044408 | -0.026591
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.045 | 719 | 1188 | 2109 | 2738 | -0.020436 | -0.018182 | -0.041364 | -0.025276
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.05 | 670 | 1118 | 1931 | 2469 | -0.020468 | -0.018437 | -0.039303 | -0.023725
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.055 | 626 | 1055 | 1781 | 2248 | -0.020344 | -0.018605 | -0.037817 | -0.022184
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.06 | 586 | 996 | 1653 | 2063 | -0.021703 | -0.020649 | -0.036152 | -0.021347
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.065 | 551 | 943 | 1543 | 1906 | -0.021314 | -0.020768 | -0.034418 | -0.020051
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.65739 | 8.1236 | 257.472 | 0.07 | 518 | 894 | 1445 | 1772 | -0.022642 | -0.020811 | -0.033445 | -0.019369
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.03 | 890 | 1576 | 3097 | 4063 | -0.019824 | -0.1151 | -0.050291 | -0.017175
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.035 | 823 | 1455 | 2711 | 3483 | -0.020238 | -0.10406 | -0.046765 | -0.016935
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.04 | 763 | 1351 | 2414 | 3047 | -0.021795 | -0.095716 | -0.04396 | -0.017097
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.045 | 710 | 1260 | 2178 | 2709 | -0.022039 | -0.089595 | -0.041795 | -0.017054
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.05 | 662 | 1180 | 1985 | 2438 | -0.022157 | -0.083851 | -0.039671 | -0.016935
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.055 | 619 | 1108 | 1825 | 2216 | -0.023659 | -0.079734 | -0.037447 | -0.017295
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.06 | 581 | 1044 | 1688 | 2031 | -0.023529 | -0.076106 | -0.035979 | -0.017417
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.065 | 546 | 985 | 1570 | 1875 | -0.023256 | -0.073377 | -0.035034 | -0.017296
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.67346 | 7.8876 | 271.872 | 0.07 | 514 | 933 | 1468 | 1741 | -0.024668 | -0.070717 | -0.034211 | -0.017494
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.03 | 777 | 1243 | 1902 | 3143 | -0.020177 | -0.018167 | -0.085577 | -0.044681
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.035 | 714 | 1159 | 1741 | 2749 | -0.020576 | -0.018628 | -0.076882 | -0.040489
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.04 | 659 | 1083 | 1607 | 2446 | -0.020802 | -0.01991 | -0.070023 | -0.037387
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.045 | 609 | 1014 | 1493 | 2205 | -0.022472 | -0.02029 | -0.06395 | -0.034588
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.05 | 566 | 951 | 1393 | 2009 | -0.022453 | -0.021605 | -0.060054 | -0.032274
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.055 | 527 | 895 | 1305 | 1846 | -0.022263 | -0.021858 | -0.056399 | -0.029953
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.06 | 492 | 843 | 1227 | 1707 | -0.02381 | -0.022042 | -0.053241 | -0.028458
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.065 | 461 | 796 | 1157 | 1588 | -0.02537 | -0.023313 | -0.050861 | -0.026961
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.67965 | 8.7578 | 271.872 | 0.07 | 434 | 753 | 1093 | 1484 | -0.022523 | -0.023346 | -0.048738 | -0.025607
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.03 | 771 | 1235 | 1833 | 3087 | -0.02033 | -0.017502 | -0.088966 | -0.045455
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.035 | 709 | 1151 | 1686 | 2704 | -0.019364 | -0.018755 | -0.078689 | -0.041135
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.04 | 653 | 1075 | 1561 | 2410 | -0.02099 | -0.019161 | -0.071938 | -0.03754
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.045 | 604 | 1006 | 1454 | 2175 | -0.022654 | -0.020448 | -0.065553 | -0.035049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.05 | 561 | 944 | 1359 | 1984 | -0.022648 | -0.020747 | -0.061464 | -0.032195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.055 | 522 | 887 | 1275 | 1824 | -0.024299 | -0.022051 | -0.05765 | -0.030303
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.06 | 488 | 836 | 1201 | 1688 | -0.024 | -0.022222 | -0.053586 | -0.028769
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.065 | 457 | 789 | 1133 | 1571 | -0.023504 | -0.022305 | -0.051883 | -0.027245
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.68756 | 8.8086 | 271.872 | 0.07 | 429 | 747 | 1072 | 1469 | -0.025 | -0.022251 | -0.049645 | -0.025862
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.03 | 765 | 1224 | 1751 | 3020 | -0.01671 | -0.016867 | -0.08564 | -0.042789
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.035 | 702 | 1141 | 1619 | 2650 | -0.018182 | -0.017227 | -0.075913 | -0.039159
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.04 | 647 | 1065 | 1506 | 2366 | -0.019697 | -0.017528 | -0.068646 | -0.035467
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.045 | 598 | 996 | 1406 | 2139 | -0.019672 | -0.018719 | -0.063291 | -0.033002
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.05 | 555 | 935 | 1318 | 1953 | -0.021164 | -0.018888 | -0.058571 | -0.030288
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.055 | 517 | 879 | 1240 | 1797 | -0.020833 | -0.018973 | -0.054157 | -0.028649
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.06 | 483 | 828 | 1169 | 1665 | -0.020284 | -0.020118 | -0.051136 | -0.026885
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.065 | 452 | 781 | 1105 | 1550 | -0.021645 | -0.021303 | -0.049053 | -0.02577
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.69681 | 8.8677 | 271.872 | 0.07 | 425 | 739 | 1046 | 1450 | -0.020737 | -0.021192 | -0.047359 | -0.024882
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.03 | 757 | 1213 | 1654 | 2941 | -0.015605 | -0.014622 | -0.083657 | -0.040457
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.035 | 694 | 1129 | 1541 | 2588 | -0.016997 | -0.015693 | -0.073361 | -0.036485
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.04 | 640 | 1054 | 1441 | 2315 | -0.016897 | -0.015873 | -0.066105 | -0.033403
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.045 | 591 | 986 | 1351 | 2096 | -0.018272 | -0.016949 | -0.060501 | -0.030975
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.05 | 548 | 924 | 1271 | 1917 | -0.019678 | -0.018066 | -0.055721 | -0.028383
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.055 | 510 | 868 | 1198 | 1766 | -0.019231 | -0.0181 | -0.051465 | -0.026997
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.06 | 477 | 818 | 1132 | 1638 | -0.018519 | -0.018007 | -0.048739 | -0.025
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.065 | 446 | 772 | 1072 | 1526 | -0.01978 | -0.01906 | -0.046263 | -0.024297
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.70853 | 8.9419 | 271.872 | 0.07 | 419 | 730 | 1016 | 1429 | -0.021028 | -0.018817 | -0.044214 | -0.02324

## 25%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | % change from normal
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | Very Slow | Slow | Moderate | Fast
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.03 | 2649 | 9801 | 10235 | 10688 | -0.019978 | -0.017148 | -0.016338 | -0.015566
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.035 | 2525 | 8401 | 8773 | 9161 | -0.020559 | -0.017197 | -0.01637 | -0.015581
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.04 | 2409 | 7351 | 7676 | 8016 | -0.021527 | -0.017115 | -0.016402 | -0.015596
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.045 | 2300 | 6534 | 6823 | 7125 | -0.022109 | -0.017148 | -0.016434 | -0.015612
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.05 | 2198 | 5881 | 6141 | 6413 | -0.023111 | -0.017048 | -0.016338 | -0.015505
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.055 | 2103 | 5346 | 5583 | 5830 | -0.023677 | -0.017279 | -0.016385 | -0.015535
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.06 | 2014 | 4901 | 5117 | 5344 | -0.024225 | -0.017048 | -0.016529 | -0.015657
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.065 | 1930 | 4524 | 4724 | 4933 | -0.02476 | -0.017163 | -0.016448 | -0.015566
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46817 | 4.334 | 185.472 | 0.07 | 1852 | 4201 | 4386 | 4580 | -0.025263 | -0.01708 | -0.016371 | -0.015689
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.03 | 2369 | 8900 | 9336 | 9795 | -0.021074 | -0.01831 | -0.01747 | -0.016468
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.035 | 2248 | 7628 | 8003 | 8395 | -0.021758 | -0.018402 | -0.017434 | -0.016633
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.04 | 2136 | 6675 | 7002 | 7346 | -0.022426 | -0.018238 | -0.017539 | -0.016468
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.045 | 2032 | 5933 | 6224 | 6530 | -0.023077 | -0.018365 | -0.017522 | -0.016566
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.05 | 1935 | 5340 | 5602 | 5877 | -0.023713 | -0.018202 | -0.017365 | -0.016566
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.055 | 1844 | 4854 | 5093 | 5342 | -0.024855 | -0.018402 | -0.017364 | -0.016568
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.06 | 1760 | 4450 | 4668 | 4897 | -0.025471 | -0.01831 | -0.01747 | -0.016667
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.065 | 1682 | 4108 | 4309 | 4521 | -0.025492 | -0.018164 | -0.017556 | -0.016533
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.4677 | 4.7879 | 185.472 | 0.07 | 1608 | 3814 | 4001 | 4198 | -0.026634 | -0.018275 | -0.017436 | -0.016401
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.03 | 2369 | 8900 | 9336 | 9795 | -0.023495 | -0.020363 | -0.019431 | -0.01834
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.035 | 2248 | 7628 | 8003 | 8395 | -0.024306 | -0.020419 | -0.01936 | -0.018358
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.04 | 2136 | 6675 | 7002 | 7346 | -0.025103 | -0.020255 | -0.019465 | -0.018308
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.045 | 2032 | 5933 | 6224 | 6530 | -0.025887 | -0.02031 | -0.019379 | -0.01834
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.05 | 1935 | 5340 | 5602 | 5877 | -0.02666 | -0.020363 | -0.019258 | -0.018373
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.055 | 1844 | 4854 | 5093 | 5342 | -0.027426 | -0.020383 | -0.019257 | -0.018376
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.06 | 1760 | 4450 | 4668 | 4897 | -0.028161 | -0.020255 | -0.019328 | -0.018441
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.065 | 1682 | 4108 | 4309 | 4521 | -0.028307 | -0.020272 | -0.019345 | -0.018241
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.46741 | 4.7864 | 185.472 | 0.07 | 1608 | 3814 | 4001 | 4198 | -0.029572 | -0.020293 | -0.019363 | -0.018241
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.03 | 2375 | 8918 | 9355 | 9813 | -0.021022 | -0.018382 | -0.017435 | -0.016536
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.035 | 2254 | 7644 | 8018 | 8411 | -0.021701 | -0.018364 | -0.017522 | -0.016487
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.04 | 2141 | 6688 | 7016 | 7359 | -0.022821 | -0.018347 | -0.017505 | -0.016571
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.045 | 2037 | 5945 | 6236 | 6542 | -0.02349 | -0.018329 | -0.017489 | -0.016536
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.05 | 1940 | 5351 | 5613 | 5888 | -0.024145 | -0.018345 | -0.017332 | -0.016536
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.055 | 1849 | 4864 | 5103 | 5352 | -0.024789 | -0.018365 | -0.017331 | -0.016538
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.06 | 1765 | 4459 | 4677 | 4906 | -0.0254 | -0.018274 | -0.017437 | -0.016637
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.065 | 1686 | 4116 | 4318 | 4529 | -0.025997 | -0.018364 | -0.017296 | -0.016504
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46706 | 4.7846 | 185.472 | 0.07 | 1613 | 3822 | 4009 | 4205 | -0.026554 | -0.018238 | -0.017402 | -0.016604
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.03 | 2375 | 8918 | 9355 | 9813 | -0.021022 | -0.018382 | -0.017435 | -0.016536
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.035 | 2254 | 7644 | 8018 | 8411 | -0.021701 | -0.018364 | -0.017522 | -0.016487
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.04 | 2141 | 6688 | 7016 | 7359 | -0.022821 | -0.018347 | -0.017505 | -0.016571
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.045 | 2037 | 5945 | 6236 | 6542 | -0.02349 | -0.018329 | -0.017489 | -0.016536
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.05 | 1940 | 5351 | 5613 | 5888 | -0.024145 | -0.018345 | -0.017332 | -0.016536
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.055 | 1849 | 4864 | 5103 | 5352 | -0.024789 | -0.018365 | -0.017331 | -0.016538
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.06 | 1765 | 4459 | 4677 | 4906 | -0.0254 | -0.018274 | -0.017437 | -0.016637
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.065 | 1686 | 4116 | 4318 | 4529 | -0.025997 | -0.018364 | -0.017296 | -0.016504
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.46673 | 4.7829 | 185.472 | 0.07 | 1613 | 3822 | 4009 | 4205 | -0.026554 | -0.018238 | -0.017402 | -0.016604
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.03 | 2246 | 8413 | 8818 | 9242 | -0.020924 | -0.018434 | -0.017602 | -0.016704
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.035 | 2133 | 7211 | 7558 | 7922 | -0.022008 | -0.018511 | -0.017548 | -0.016634
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.04 | 2028 | 6310 | 6613 | 6931 | -0.022651 | -0.018357 | -0.017677 | -0.01674
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.045 | 1930 | 5608 | 5878 | 6161 | -0.023773 | -0.018551 | -0.017714 | -0.016757
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.05 | 1839 | 5048 | 5291 | 5545 | -0.024403 | -0.018472 | -0.017456 | -0.01667
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.055 | 1755 | 4589 | 4810 | 5041 | -0.025 | -0.018396 | -0.017565 | -0.016774
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.06 | 1676 | 4206 | 4409 | 4621 | -0.025581 | -0.018665 | -0.017602 | -0.016809
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.065 | 1602 | 3883 | 4070 | 4265 | -0.02614 | -0.018453 | -0.01762 | -0.016828
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.46609 | 4.6972 | 199.872 | 0.07 | 1533 | 3605 | 3779 | 3961 | -0.026667 | -0.018513 | -0.017676 | -0.016634
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.03 | 2008 | 7623 | 8029 | 8457 | -0.021919 | -0.01955 | -0.01858 | -0.017542
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.035 | 1899 | 6534 | 6882 | 7249 | -0.022645 | -0.019508 | -0.01854 | -0.017484
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.04 | 1798 | 5717 | 6022 | 6343 | -0.023357 | -0.019551 | -0.018579 | -0.017503
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.045 | 1704 | 5082 | 5353 | 5638 | -0.024614 | -0.019487 | -0.018519 | -0.017599
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.05 | 1618 | 4574 | 4817 | 5074 | -0.024714 | -0.019507 | -0.018541 | -0.017619
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.055 | 1538 | 4158 | 4379 | 4613 | -0.025349 | -0.019571 | -0.018602 | -0.017465
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.06 | 1463 | 3811 | 4014 | 4228 | -0.026613 | -0.019552 | -0.018582 | -0.017658
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.065 | 1394 | 3518 | 3706 | 3903 | -0.027216 | -0.019509 | -0.018538 | -0.017619
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.4661 | 5.1916 | 199.872 | 0.07 | 1330 | 3267 | 3441 | 3624 | -0.027778 | -0.019508 | -0.01854 | -0.01762
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.03 | 2008 | 7623 | 8029 | 8457 | -0.021919 | -0.01955 | -0.01858 | -0.017542
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.035 | 1899 | 6534 | 6882 | 7249 | -0.022645 | -0.019508 | -0.01854 | -0.017484
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.04 | 1798 | 5717 | 6022 | 6343 | -0.023357 | -0.019551 | -0.018579 | -0.017503
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.045 | 1704 | 5082 | 5353 | 5638 | -0.024614 | -0.019487 | -0.018519 | -0.017599
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.05 | 1618 | 4574 | 4817 | 5074 | -0.024714 | -0.019507 | -0.018541 | -0.017619
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.055 | 1538 | 4158 | 4379 | 4613 | -0.025349 | -0.019571 | -0.018602 | -0.017465
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.06 | 1463 | 3811 | 4014 | 4228 | -0.026613 | -0.019552 | -0.018582 | -0.017658
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.065 | 1394 | 3518 | 3706 | 3903 | -0.027216 | -0.019509 | -0.018538 | -0.017619
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.46633 | 5.1929 | 199.872 | 0.07 | 1330 | 3267 | 3441 | 3624 | -0.027778 | -0.019508 | -0.01854 | -0.01762
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.03 | 2008 | 7623 | 8029 | 8457 | -0.02001 | -0.017528 | -0.016656 | -0.015827
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.035 | 1899 | 6534 | 6882 | 7249 | -0.020629 | -0.017591 | -0.016717 | -0.01575
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.04 | 1798 | 5717 | 6022 | 6343 | -0.02123 | -0.017698 | -0.016656 | -0.015673
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.045 | 1704 | 5082 | 5353 | 5638 | -0.021814 | -0.017591 | -0.016716 | -0.015712
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.05 | 1618 | 4574 | 4817 | 5074 | -0.022356 | -0.017612 | -0.016738 | -0.015904
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.055 | 1538 | 4158 | 4379 | 4613 | -0.022872 | -0.017486 | -0.016839 | -0.015788
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.06 | 1463 | 3811 | 4014 | 4228 | -0.024016 | -0.017784 | -0.016899 | -0.015829
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.065 | 1394 | 3518 | 3706 | 3903 | -0.024493 | -0.017593 | -0.016715 | -0.015885
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.46628 | 5.1926 | 199.872 | 0.07 | 1330 | 3267 | 3441 | 3624 | -0.024927 | -0.017444 | -0.016576 | -0.01602
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.03 | 2008 | 7623 | 8029 | 8457 | -0.02001 | -0.017528 | -0.016656 | -0.015827
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.035 | 1899 | 6534 | 6882 | 7249 | -0.020629 | -0.017591 | -0.016717 | -0.01575
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.04 | 1798 | 5717 | 6022 | 6343 | -0.02123 | -0.017698 | -0.016656 | -0.015673
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.045 | 1704 | 5082 | 5353 | 5638 | -0.021814 | -0.017591 | -0.016716 | -0.015712
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.05 | 1618 | 4574 | 4817 | 5074 | -0.022356 | -0.017612 | -0.016738 | -0.015904
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.055 | 1538 | 4158 | 4379 | 4613 | -0.022872 | -0.017486 | -0.016839 | -0.015788
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.06 | 1463 | 3811 | 4014 | 4228 | -0.024016 | -0.017784 | -0.016899 | -0.015829
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.065 | 1394 | 3518 | 3706 | 3903 | -0.024493 | -0.017593 | -0.016715 | -0.015885
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.46631 | 5.1928 | 199.872 | 0.07 | 1330 | 3267 | 3441 | 3624 | -0.024927 | -0.017444 | -0.016576 | -0.01602
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.03 | 1920 | 7267 | 7645 | 8044 | -0.019908 | -0.017707 | -0.016973 | -0.016024
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.035 | 1817 | 6229 | 6553 | 6895 | -0.020485 | -0.017663 | -0.016952 | -0.015984
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.04 | 1722 | 5450 | 5734 | 6033 | -0.021591 | -0.017841 | -0.016972 | -0.015984
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.045 | 1633 | 4845 | 5097 | 5363 | -0.022741 | -0.01764 | -0.016972 | -0.015963
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.05 | 1552 | 4360 | 4587 | 4826 | -0.02267 | -0.017797 | -0.016931 | -0.016106
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.055 | 1476 | 3964 | 4170 | 4388 | -0.02381 | -0.017596 | -0.016973 | -0.015923
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.06 | 1406 | 3633 | 3823 | 4022 | -0.024289 | -0.017843 | -0.016718 | -0.015904
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.065 | 1341 | 3354 | 3529 | 3713 | -0.024727 | -0.017862 | -0.016718 | -0.015902
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.46861 | 5.0836 | 214.272 | 0.07 | 1280 | 3114 | 3277 | 3447 | -0.025133 | -0.017975 | -0.016802 | -0.015986
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.03 | 1709 | 6546 | 6924 | 7324 | -0.02063 | -0.018738 | -0.017872 | -0.016913
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.035 | 1610 | 5611 | 5935 | 6278 | -0.021277 | -0.018713 | -0.017872 | -0.016758
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.04 | 1518 | 4909 | 5193 | 5493 | -0.022537 | -0.018789 | -0.017779 | -0.016825
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.045 | 1435 | 4364 | 4616 | 4883 | -0.02248 | -0.018664 | -0.017872 | -0.016714
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.05 | 1357 | 3927 | 4154 | 4395 | -0.023741 | -0.018986 | -0.017967 | -0.016779
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.055 | 1286 | 3570 | 3777 | 3995 | -0.025019 | -0.018961 | -0.017685 | -0.016736
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.06 | 1221 | 3273 | 3462 | 3662 | -0.02476 | -0.018885 | -0.017872 | -0.016913
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.065 | 1160 | 3021 | 3196 | 3380 | -0.026029 | -0.018837 | -0.017824 | -0.01687
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.46924 | 5.6225 | 214.272 | 0.07 | 1104 | 2805 | 2967 | 3139 | -0.026455 | -0.018888 | -0.017875 | -0.016912
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.03 | 1706 | 6533 | 6912 | 7312 | -0.02235 | -0.020687 | -0.019574 | -0.018523
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.035 | 1606 | 5600 | 5924 | 6267 | -0.023708 | -0.020637 | -0.019692 | -0.018481
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.04 | 1515 | 4900 | 5184 | 5484 | -0.024469 | -0.020588 | -0.019482 | -0.018436
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.045 | 1431 | 4356 | 4608 | 4875 | -0.025204 | -0.020463 | -0.019574 | -0.018325
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.05 | 1354 | 3920 | 4147 | 4387 | -0.025899 | -0.020734 | -0.019622 | -0.018568
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.055 | 1283 | 3564 | 3770 | 3988 | -0.027293 | -0.02061 | -0.019506 | -0.018459
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.06 | 1218 | 3267 | 3456 | 3656 | -0.027157 | -0.020683 | -0.019574 | -0.018523
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.065 | 1157 | 3015 | 3190 | 3375 | -0.028547 | -0.020786 | -0.019668 | -0.018325
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.46997 | 5.6269 | 214.272 | 0.07 | 1101 | 2800 | 2962 | 3134 | -0.029101 | -0.020637 | -0.01953 | -0.018478
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.03 | 1706 | 6533 | 6912 | 7312 | -0.020666 | -0.018774 | -0.017763 | -0.016808
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.035 | 1606 | 5600 | 5924 | 6267 | -0.021328 | -0.018749 | -0.017905 | -0.016941
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.04 | 1515 | 4900 | 5184 | 5484 | -0.022581 | -0.018823 | -0.01781 | -0.016852
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.045 | 1431 | 4356 | 4608 | 4875 | -0.023208 | -0.018698 | -0.017693 | -0.016741
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.05 | 1354 | 3920 | 4147 | 4387 | -0.023792 | -0.018773 | -0.017764 | -0.016809
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.055 | 1283 | 3564 | 3770 | 3988 | -0.024335 | -0.018722 | -0.017718 | -0.017008
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.06 | 1218 | 3267 | 3456 | 3656 | -0.02482 | -0.018624 | -0.017624 | -0.01694
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.065 | 1157 | 3015 | 3190 | 3375 | -0.026094 | -0.018874 | -0.017857 | -0.016608
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.47084 | 5.6321 | 214.272 | 0.07 | 1101 | 2800 | 2962 | 3134 | -0.026525 | -0.018921 | -0.017905 | -0.01663
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.03 | 1702 | 6521 | 6899 | 7300 | -0.022962 | -0.020577 | -0.019611 | -0.018421
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.035 | 1603 | 5589 | 5914 | 6257 | -0.023157 | -0.020676 | -0.019562 | -0.01851
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.04 | 1512 | 4891 | 5175 | 5475 | -0.024516 | -0.020625 | -0.019515 | -0.018465
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.045 | 1428 | 4347 | 4600 | 4866 | -0.025256 | -0.020725 | -0.019399 | -0.018556
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.05 | 1351 | 3913 | 4140 | 4380 | -0.025955 | -0.020526 | -0.019422 | -0.018377
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.055 | 1280 | 3557 | 3763 | 3982 | -0.026616 | -0.02065 | -0.019541 | -0.018487
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.06 | 1215 | 3260 | 3450 | 3650 | -0.027222 | -0.020727 | -0.019329 | -0.018553
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.065 | 1154 | 3010 | 3184 | 3369 | -0.02862 | -0.020501 | -0.019704 | -0.018357
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.47199 | 5.639 | 214.272 | 0.07 | 1098 | 2795 | 2957 | 3128 | -0.029178 | -0.020673 | -0.019562 | -0.018513
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.03 | 1632 | 6239 | 6594 | 6969 | -0.022754 | -0.020873 | -0.019771 | -0.018589
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.035 | 1538 | 5348 | 5652 | 5973 | -0.024112 | -0.020871 | -0.019771 | -0.018728
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.04 | 1452 | 4679 | 4945 | 5227 | -0.024849 | -0.020925 | -0.019822 | -0.018588
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.045 | 1373 | 4159 | 4396 | 4646 | -0.02555 | -0.020951 | -0.019625 | -0.018589
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.05 | 1300 | 3743 | 3956 | 4181 | -0.026217 | -0.020926 | -0.019822 | -0.018775
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.055 | 1232 | 3403 | 3597 | 3801 | -0.027624 | -0.021001 | -0.019624 | -0.01859
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.06 | 1170 | 3120 | 3297 | 3484 | -0.028239 | -0.020716 | -0.019625 | -0.018868
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.065 | 1113 | 2880 | 3043 | 3216 | -0.028796 | -0.020741 | -0.019968 | -0.018914
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.48051 | 5.5264 | 228.672 | 0.07 | 1060 | 2674 | 2826 | 2987 | -0.029304 | -0.020871 | -0.019771 | -0.018403
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.03 | 1449 | 5471 | 5944 | 6319 | -0.020946 | -0.039333 | -0.018818 | -0.017721
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.035 | 1358 | 4697 | 5095 | 5416 | -0.022318 | -0.037697 | -0.018683 | -0.017773
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.04 | 1276 | 4116 | 4458 | 4739 | -0.022971 | -0.036517 | -0.01871 | -0.017824
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.045 | 1201 | 3663 | 3963 | 4213 | -0.023577 | -0.035545 | -0.018574 | -0.01772
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.05 | 1132 | 3300 | 3566 | 3791 | -0.024978 | -0.034523 | -0.018982 | -0.017876
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.055 | 1070 | 3003 | 3242 | 3447 | -0.024613 | -0.033473 | -0.018765 | -0.017669
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.06 | 1012 | 2754 | 2972 | 3159 | -0.025987 | -0.033006 | -0.018818 | -0.017724
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.065 | 959 | 2545 | 2743 | 2916 | -0.026396 | -0.032319 | -0.018956 | -0.017851
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.48296 | 6.1237 | 228.672 | 0.07 | 911 | 2364 | 2547 | 2708 | -0.026709 | -0.031941 | -0.018875 | -0.017773
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.03 | 1443 | 5430 | 5923 | 6299 | -0.021031 | -0.039618 | -0.018884 | -0.017623
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.035 | 1353 | 4663 | 5077 | 5399 | -0.022399 | -0.03816 | -0.018748 | -0.017649
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.04 | 1271 | 4088 | 4443 | 4724 | -0.023059 | -0.036531 | -0.018772 | -0.017675
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.045 | 1196 | 3639 | 3949 | 4199 | -0.023673 | -0.035516 | -0.018638 | -0.017778
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.05 | 1127 | 3279 | 3554 | 3779 | -0.025087 | -0.034737 | -0.018774 | -0.017676
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.055 | 1065 | 2984 | 3231 | 3436 | -0.024725 | -0.033679 | -0.018828 | -0.017444
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.06 | 1007 | 2737 | 2962 | 3149 | -0.026112 | -0.033204 | -0.018555 | -0.017779
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.065 | 955 | 2529 | 2734 | 2907 | -0.026504 | -0.032887 | -0.018665 | -0.017574
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.48588 | 6.1421 | 228.672 | 0.07 | 906 | 2350 | 2539 | 2699 | -0.026853 | -0.032125 | -0.018554 | -0.017831
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.03 | 1437 | 5390 | 5903 | 6278 | -0.021784 | -0.039729 | -0.018783 | -0.017681
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.035 | 1347 | 4630 | 5060 | 5381 | -0.022496 | -0.038222 | -0.018619 | -0.017707
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.04 | 1265 | 4059 | 4427 | 4709 | -0.023166 | -0.037011 | -0.018839 | -0.017526
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.045 | 1191 | 3614 | 3935 | 4186 | -0.02377 | -0.03601 | -0.018948 | -0.017602
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.05 | 1122 | 3257 | 3542 | 3767 | -0.025195 | -0.034963 | -0.018837 | -0.017731
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.055 | 1060 | 2965 | 3220 | 3425 | -0.024839 | -0.033887 | -0.018592 | -0.017499
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.06 | 1003 | 2720 | 2952 | 3139 | -0.025267 | -0.033404 | -0.018617 | -0.017835
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.065 | 950 | 2514 | 2725 | 2898 | -0.026639 | -0.032705 | -0.018725 | -0.017627
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.48895 | 6.1615 | 228.672 | 0.07 | 902 | 2335 | 2530 | 2691 | -0.026969 | -0.032726 | -0.018619 | -0.017525
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.03 | 1432 | 5349 | 5883 | 6258 | -0.021189 | -0.040194 | -0.018682 | -0.017582
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.035 | 1342 | 4596 | 5043 | 5364 | -0.021866 | -0.038695 | -0.018681 | -0.017582
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.04 | 1260 | 4031 | 4412 | 4694 | -0.023256 | -0.037258 | -0.018683 | -0.017581
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.045 | 1185 | 3590 | 3922 | 4172 | -0.023888 | -0.035983 | -0.018764 | -0.01766
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.05 | 1117 | 3236 | 3530 | 3755 | -0.024454 | -0.035182 | -0.018627 | -0.01753
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.055 | 1055 | 2946 | 3209 | 3413 | -0.024954 | -0.034098 | -0.018654 | -0.017842
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.06 | 998 | 2703 | 2942 | 3129 | -0.025391 | -0.033607 | -0.018679 | -0.017582
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.065 | 945 | 2498 | 2715 | 2888 | -0.026777 | -0.033282 | -0.018793 | -0.017687
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.49264 | 6.1847 | 228.672 | 0.07 | 897 | 2321 | 2521 | 2682 | -0.027115 | -0.032514 | -0.018684 | -0.017582
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.03 | 1365 | 5166 | 5601 | 5954 | -0.023605 | -0.040847 | -0.020633 | -0.019433
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.035 | 1280 | 4435 | 4801 | 5104 | -0.02439 | -0.03942 | -0.020604 | -0.019216
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.04 | 1203 | 3885 | 4201 | 4466 | -0.025122 | -0.038366 | -0.020518 | -0.019324
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.045 | 1132 | 3457 | 3734 | 3970 | -0.026655 | -0.037316 | -0.020462 | -0.019269
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.05 | 1068 | 3115 | 3361 | 3573 | -0.026436 | -0.0362 | -0.020402 | -0.019215
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.055 | 1009 | 2834 | 3055 | 3248 | -0.027001 | -0.035398 | -0.020519 | -0.019324
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.06 | 954 | 2600 | 2801 | 2977 | -0.028513 | -0.034534 | -0.020287 | -0.019433
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.065 | 905 | 2401 | 2585 | 2748 | -0.02897 | -0.034191 | -0.020462 | -0.019272
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.51386 | 6.1065 | 243.072 | 0.07 | 859 | 2231 | 2401 | 2552 | -0.029379 | -0.033362 | -0.0204 | -0.019216
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.03 | 1200 | 3847 | 4990 | 5341 | -0.022801 | -0.060562 | -0.021185 | -0.01982
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.035 | 1119 | 3346 | 4277 | 4578 | -0.024412 | -0.05773 | -0.021057 | -0.01991
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.04 | 1046 | 2965 | 3742 | 4006 | -0.025163 | -0.055432 | -0.021188 | -0.019819
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.045 | 979 | 2664 | 3327 | 3561 | -0.026839 | -0.052968 | -0.020895 | -0.019818
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.05 | 919 | 2419 | 2994 | 3205 | -0.027513 | -0.051373 | -0.021249 | -0.019578
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.055 | 865 | 2216 | 2722 | 2913 | -0.026997 | -0.05015 | -0.020863 | -0.019852
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.06 | 815 | 2044 | 2495 | 2670 | -0.028605 | -0.04886 | -0.021185 | -0.020183
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.065 | 770 | 1897 | 2303 | 2465 | -0.029004 | -0.047691 | -0.021249 | -0.019881
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.52148 | 6.7992 | 243.072 | 0.07 | 728 | 1770 | 2139 | 2289 | -0.030626 | -0.04685 | -0.021053 | -0.0197
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.03 | 1187 | 3732 | 4941 | 5292 | -0.023045 | -0.062547 | -0.021003 | -0.019818
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.035 | 1106 | 3252 | 4235 | 4536 | -0.024691 | -0.0593 | -0.021036 | -0.019879
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.04 | 1033 | 2885 | 3706 | 3969 | -0.025472 | -0.056881 | -0.02113 | -0.019758
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.045 | 967 | 2595 | 3294 | 3528 | -0.026183 | -0.0543 | -0.0211 | -0.019728
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.05 | 908 | 2359 | 2965 | 3175 | -0.026795 | -0.05261 | -0.020806 | -0.019759
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.055 | 854 | 2162 | 2695 | 2887 | -0.027335 | -0.051338 | -0.021068 | -0.019694
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.06 | 804 | 1996 | 2471 | 2646 | -0.028986 | -0.049976 | -0.020998 | -0.019637
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.065 | 760 | 1854 | 2281 | 2443 | -0.028133 | -0.048255 | -0.02103 | -0.019663
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.53114 | 6.8619 | 243.072 | 0.07 | 719 | 1730 | 2118 | 2268 | -0.028378 | -0.047881 | -0.020804 | -0.019879
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.03 | 1170 | 3579 | 4877 | 5228 | -0.023372 | -0.065047 | -0.021076 | -0.019689
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.035 | 1090 | 3126 | 4181 | 4481 | -0.024172 | -0.061543 | -0.020843 | -0.019689
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.04 | 1017 | 2779 | 3658 | 3921 | -0.024928 | -0.058604 | -0.020878 | -0.01975
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.045 | 952 | 2503 | 3252 | 3485 | -0.025589 | -0.056184 | -0.020777 | -0.019691
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.05 | 893 | 2278 | 2926 | 3137 | -0.026172 | -0.054379 | -0.021077 | -0.019688
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.055 | 839 | 2091 | 2660 | 2852 | -0.02781 | -0.05256 | -0.020979 | -0.019594
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.06 | 790 | 1932 | 2439 | 2614 | -0.02829 | -0.051081 | -0.020875 | -0.019505
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.065 | 746 | 1795 | 2251 | 2413 | -0.028646 | -0.050265 | -0.020879 | -0.019504
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.54284 | 6.9371 | 243.072 | 0.07 | 706 | 1677 | 2090 | 2241 | -0.028886 | -0.04878 | -0.021077 | -0.019256
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.03 | 1152 | 3407 | 4784 | 5157 | -0.020408 | -0.063239 | -0.023873 | -0.018088
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.035 | 1072 | 2984 | 4103 | 4420 | -0.021898 | -0.059565 | -0.023328 | -0.018214
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.04 | 1000 | 2658 | 3592 | 3868 | -0.022483 | -0.057112 | -0.022851 | -0.018025
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.045 | 935 | 2399 | 3194 | 3438 | -0.024008 | -0.054395 | -0.022345 | -0.017995
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.05 | 877 | 2187 | 2875 | 3094 | -0.023385 | -0.052426 | -0.022441 | -0.018089
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.055 | 823 | 2010 | 2615 | 2813 | -0.026036 | -0.050992 | -0.021698 | -0.01815
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.06 | 775 | 1859 | 2397 | 2579 | -0.026382 | -0.049591 | -0.022032 | -0.017898
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.065 | 731 | 1730 | 2213 | 2380 | -0.026631 | -0.047881 | -0.021662 | -0.018152
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.55815 | 7.0342 | 243.072 | 0.07 | 691 | 1616 | 2056 | 2210 | -0.026761 | -0.047731 | -0.021418 | -0.018214
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.03 | 1081 | 3163 | 4473 | 4847 | -0.016379 | -0.048722 | -0.023789 | -0.013434
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.035 | 1006 | 2773 | 3838 | 4154 | -0.016618 | -0.046096 | -0.022912 | -0.013536
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.04 | 939 | 2472 | 3361 | 3635 | -0.016754 | -0.044084 | -0.022112 | -0.013569
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.045 | 878 | 2233 | 2990 | 3231 | -0.016797 | -0.042042 | -0.021277 | -0.013435
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.05 | 822 | 2036 | 2693 | 2908 | -0.019093 | -0.040528 | -0.020371 | -0.013569
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.055 | 773 | 1872 | 2449 | 2644 | -0.017789 | -0.039014 | -0.020008 | -0.013433
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.06 | 727 | 1732 | 2246 | 2423 | -0.018893 | -0.038312 | -0.019642 | -0.013838
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.065 | 686 | 1613 | 2075 | 2237 | -0.02 | -0.037015 | -0.018913 | -0.013668
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60689 | 7.0619 | 257.472 | 0.07 | 648 | 1507 | 1927 | 2077 | -0.021148 | -0.036445 | -0.018839 | -0.01377
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.03 | 928 | 1520 | 3154 | 4241 | -0.012766 | -0.087087 | -0.035474 | -0.011422
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.035 | 858 | 1418 | 2768 | 3635 | -0.012658 | -0.077424 | -0.032844 | -0.011422
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.04 | 795 | 1327 | 2471 | 3181 | -0.013648 | -0.070077 | -0.0306 | -0.011498
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.045 | 739 | 1245 | 2233 | 2828 | -0.014667 | -0.064613 | -0.02913 | -0.011189
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.05 | 689 | 1170 | 2039 | 2545 | -0.014306 | -0.060995 | -0.027659 | -0.011267
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.055 | 644 | 1102 | 1876 | 2313 | -0.015291 | -0.05812 | -0.025961 | -0.011538
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.06 | 604 | 1041 | 1737 | 2121 | -0.014682 | -0.055354 | -0.025253 | -0.011189
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.065 | 567 | 986 | 1618 | 1958 | -0.015625 | -0.052834 | -0.024125 | -0.011111
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.63214 | 7.966 | 257.472 | 0.07 | 534 | 934 | 1513 | 1818 | -0.016575 | -0.050813 | -0.023241 | -0.011419
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.03 | 919 | 1459 | 3067 | 4187 | -0.0096983 | -0.040132 | -0.027584 | -0.012733
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.035 | 849 | 1367 | 2698 | 3592 | -0.01049 | -0.035966 | -0.025289 | -0.011829
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.04 | 787 | 1282 | 2412 | 3144 | -0.010063 | -0.033911 | -0.023877 | -0.011632
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.045 | 731 | 1206 | 2184 | 2796 | -0.010825 | -0.031325 | -0.021944 | -0.011315
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.05 | 681 | 1135 | 1996 | 2518 | -0.011611 | -0.029915 | -0.021089 | -0.010609
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.055 | 637 | 1071 | 1838 | 2290 | -0.01087 | -0.028131 | -0.020256 | -0.0099438
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.06 | 597 | 1013 | 1704 | 2100 | -0.011589 | -0.026897 | -0.018998 | -0.009901
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.065 | 560 | 959 | 1588 | 1938 | -0.012346 | -0.027383 | -0.018541 | -0.010215
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.64295 | 8.0338 | 257.472 | 0.07 | 528 | 910 | 1486 | 1800 | -0.011236 | -0.025696 | -0.017845 | -0.009901
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.03 | 916 | 1455 | 3037 | 4164 | -0.0097297 | -0.019542 | -0.027849 | -0.01537
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.035 | 846 | 1362 | 2674 | 3573 | -0.010526 | -0.018732 | -0.025865 | -0.014345
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.04 | 784 | 1278 | 2393 | 3129 | -0.010101 | -0.018433 | -0.023664 | -0.013556
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.045 | 728 | 1201 | 2167 | 2783 | -0.01087 | -0.017989 | -0.022553 | -0.013121
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.05 | 679 | 1132 | 1982 | 2507 | -0.010204 | -0.016507 | -0.021235 | -0.012214
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.055 | 634 | 1068 | 1825 | 2281 | -0.01092 | -0.015668 | -0.020397 | -0.01127
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.06 | 594 | 1009 | 1693 | 2092 | -0.011647 | -0.016569 | -0.019119 | -0.010875
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.065 | 558 | 956 | 1578 | 1931 | -0.012389 | -0.016461 | -0.018657 | -0.010758
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.64563 | 8.0506 | 257.472 | 0.07 | 526 | 906 | 1477 | 1794 | -0.011278 | -0.016287 | -0.017952 | -0.01048
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.03 | 913 | 1451 | 3008 | 4140 | -0.0097614 | -0.0088798 | -0.028424 | -0.016861
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.035 | 843 | 1358 | 2651 | 3554 | -0.010563 | -0.0094821 | -0.025726 | -0.015785
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.04 | 781 | 1274 | 2373 | 3113 | -0.010139 | -0.0093313 | -0.02426 | -0.014562
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.045 | 726 | 1197 | 2150 | 2770 | -0.010899 | -0.010744 | -0.022727 | -0.013884
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.05 | 676 | 1128 | 1967 | 2496 | -0.011696 | -0.0096576 | -0.021393 | -0.013049
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.055 | 632 | 1064 | 1813 | 2271 | -0.010955 | -0.010233 | -0.020529 | -0.012179
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.06 | 592 | 1006 | 1681 | 2084 | -0.011686 | -0.010816 | -0.019825 | -0.011385
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.065 | 556 | 952 | 1568 | 1924 | -0.012433 | -0.011423 | -0.018773 | -0.010797
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.64887 | 8.0708 | 257.472 | 0.07 | 524 | 903 | 1468 | 1788 | -0.011321 | -0.010953 | -0.01806 | -0.010515
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.03 | 899 | 1679 | 3179 | 4098 | -0.0099119 | -0.057271 | -0.025146 | -0.0087083
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.035 | 832 | 1540 | 2777 | 3513 | -0.0095238 | -0.051724 | -0.023558 | -0.0084674
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.04 | 772 | 1423 | 2470 | 3074 | -0.010256 | -0.047523 | -0.021782 | -0.0083871
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.045 | 718 | 1322 | 2225 | 2732 | -0.011019 | -0.044798 | -0.021117 | -0.0087083
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.05 | 670 | 1234 | 2026 | 2459 | -0.01034 | -0.041925 | -0.019836 | -0.0084677
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.055 | 627 | 1156 | 1860 | 2235 | -0.011041 | -0.039867 | -0.018987 | -0.0088692
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.06 | 588 | 1087 | 1720 | 2049 | -0.011765 | -0.038053 | -0.017704 | -0.0087083
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.065 | 553 | 1024 | 1599 | 1891 | -0.010733 | -0.036689 | -0.01721 | -0.0089099
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.66438 | 7.8342 | 271.872 | 0.07 | 521 | 968 | 1494 | 1756 | -0.011385 | -0.035857 | -0.017105 | -0.0090293
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.03 | 784 | 1254 | 1984 | 3211 | -0.011349 | -0.0094787 | -0.046154 | -0.024012
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.035 | 721 | 1169 | 1808 | 2802 | -0.010974 | -0.010161 | -0.041357 | -0.02199
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.04 | 665 | 1093 | 1663 | 2490 | -0.011887 | -0.01086 | -0.037616 | -0.020071
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.045 | 616 | 1024 | 1540 | 2242 | -0.011236 | -0.010628 | -0.034483 | -0.018389
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.05 | 572 | 961 | 1434 | 2040 | -0.01209 | -0.011317 | -0.032389 | -0.017341
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.055 | 533 | 904 | 1341 | 1872 | -0.011132 | -0.012022 | -0.030369 | -0.01629
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.06 | 498 | 852 | 1259 | 1730 | -0.011905 | -0.011601 | -0.028549 | -0.015367
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.065 | 467 | 805 | 1186 | 1608 | -0.012685 | -0.01227 | -0.027071 | -0.014706
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.67053 | 8.6988 | 271.872 | 0.07 | 438 | 761 | 1119 | 1502 | -0.013514 | -0.01297 | -0.02611 | -0.013789
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.03 | 778 | 1245 | 1915 | 3155 | -0.011436 | -0.0095465 | -0.048211 | -0.024428
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.035 | 715 | 1161 | 1752 | 2758 | -0.011065 | -0.01023 | -0.042623 | -0.021986
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.04 | 660 | 1084 | 1617 | 2453 | -0.010495 | -0.010949 | -0.038644 | -0.020367
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.045 | 610 | 1015 | 1501 | 2212 | -0.012945 | -0.011685 | -0.035347 | -0.018634
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.05 | 567 | 953 | 1400 | 2014 | -0.012195 | -0.011411 | -0.033149 | -0.017561
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.055 | 528 | 896 | 1311 | 1850 | -0.013084 | -0.012128 | -0.031042 | -0.016481
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.06 | 493 | 845 | 1232 | 1711 | -0.014 | -0.011696 | -0.029157 | -0.015535
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.065 | 462 | 798 | 1162 | 1591 | -0.012821 | -0.011152 | -0.027615 | -0.014861
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.67853 | 8.7506 | 271.872 | 0.07 | 434 | 755 | 1098 | 1487 | -0.013636 | -0.01178 | -0.026596 | -0.013926
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.03 | 771 | 1235 | 1833 | 3087 | -0.0089974 | -0.0080321 | -0.04282 | -0.021553
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.035 | 709 | 1151 | 1686 | 2704 | -0.0083916 | -0.0086133 | -0.037671 | -0.019579
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.04 | 653 | 1075 | 1561 | 2410 | -0.010606 | -0.0083026 | -0.034632 | -0.01753
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.045 | 604 | 1006 | 1454 | 2175 | -0.0098361 | -0.008867 | -0.031312 | -0.016727
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.05 | 561 | 944 | 1359 | 1984 | -0.010582 | -0.0094439 | -0.029286 | -0.014896
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.055 | 522 | 887 | 1275 | 1824 | -0.011364 | -0.010045 | -0.02746 | -0.014054
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.06 | 488 | 836 | 1201 | 1688 | -0.010142 | -0.010651 | -0.025162 | -0.013442
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.065 | 457 | 789 | 1133 | 1571 | -0.010823 | -0.011278 | -0.024957 | -0.012571
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.68812 | 8.8122 | 271.872 | 0.07 | 429 | 747 | 1072 | 1469 | -0.011521 | -0.010596 | -0.023679 | -0.012105
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.03 | 762 | 1221 | 1723 | 2997 | -0.0091027 | -0.0081235 | -0.045429 | -0.022186
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.035 | 700 | 1137 | 1597 | 2632 | -0.0084986 | -0.0087184 | -0.039687 | -0.020104
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.04 | 645 | 1062 | 1487 | 2351 | -0.0092166 | -0.0084034 | -0.036293 | -0.018372
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.045 | 596 | 993 | 1391 | 2127 | -0.0099668 | -0.0099701 | -0.032684 | -0.016644
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.05 | 553 | 932 | 1305 | 1943 | -0.010733 | -0.0095643 | -0.030461 | -0.015205
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.055 | 515 | 876 | 1228 | 1788 | -0.0096154 | -0.0090498 | -0.027712 | -0.014876
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.06 | 481 | 825 | 1158 | 1657 | -0.010288 | -0.0096038 | -0.026891 | -0.01369
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.065 | 450 | 778 | 1095 | 1543 | -0.010989 | -0.011436 | -0.025801 | -0.013427
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.7006 | 8.8917 | 271.872 | 0.07 | 423 | 736 | 1037 | 1444 | -0.011682 | -0.010753 | -0.024459 | -0.012987

## 50%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | % change from normal
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips | Very Slow | Slow | Moderate | Fast
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.03 | 2596 | 9635 | 10069 | 10523 | -0.039586 | -0.033795 | -0.032292 | -0.030764
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.035 | 2473 | 8258 | 8630 | 9020 | -0.040729 | -0.033926 | -0.032403 | -0.030733
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.04 | 2357 | 7226 | 7552 | 7892 | -0.042648 | -0.033828 | -0.032291 | -0.030824
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.045 | 2249 | 6423 | 6713 | 7015 | -0.043793 | -0.033845 | -0.032291 | -0.03081
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.05 | 2149 | 5781 | 6041 | 6314 | -0.044889 | -0.033762 | -0.032356 | -0.030703
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.055 | 2054 | 5255 | 5492 | 5740 | -0.046425 | -0.034007 | -0.032417 | -0.030733
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.06 | 1966 | 4817 | 5034 | 5261 | -0.047481 | -0.033895 | -0.032481 | -0.030945
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.065 | 1883 | 4447 | 4647 | 4857 | -0.048509 | -0.033891 | -0.03248 | -0.030732
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48487 | 4.4107 | 185.472 | 0.07 | 1805 | 4129 | 4315 | 4510 | -0.05 | -0.033926 | -0.032294 | -0.030733
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652 | -0.038843 | -0.034194 | -0.032519 | -0.030826
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273 | -0.04047 | -0.03423 | -0.032535 | -0.030924
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239 | -0.041648 | -0.034123 | -0.032552 | -0.030794
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435 | -0.043269 | -0.034249 | -0.032518 | -0.030873
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791 | -0.0444 | -0.034014 | -0.03245 | -0.030957
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265 | -0.046007 | -0.034176 | -0.032607 | -0.030744
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826 | -0.047065 | -0.034194 | -0.032625 | -0.030924
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455 | -0.048088 | -0.034178 | -0.032604 | -0.03089
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48433 | 4.8722 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136 | -0.049031 | -0.033977 | -0.032417 | -0.030928
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652 | -0.04122 | -0.036214 | -0.03445 | -0.032672
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273 | -0.042969 | -0.036214 | -0.034432 | -0.032624
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239 | -0.044272 | -0.036107 | -0.034449 | -0.032607
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435 | -0.046021 | -0.036162 | -0.034347 | -0.032622
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791 | -0.047284 | -0.03614 | -0.034314 | -0.032738
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265 | -0.048523 | -0.036125 | -0.034469 | -0.032525
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826 | -0.049696 | -0.036107 | -0.034454 | -0.032672
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455 | -0.050838 | -0.036251 | -0.034365 | -0.032573
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48398 | 4.8705 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136 | -0.051901 | -0.035962 | -0.034314 | -0.032741
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652 | -0.04122 | -0.036214 | -0.03445 | -0.032672
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273 | -0.042969 | -0.036214 | -0.034432 | -0.032624
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239 | -0.044272 | -0.036107 | -0.034449 | -0.032607
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435 | -0.046021 | -0.036162 | -0.034347 | -0.032622
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791 | -0.047284 | -0.03614 | -0.034314 | -0.032738
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265 | -0.048523 | -0.036125 | -0.034469 | -0.032525
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826 | -0.049696 | -0.036107 | -0.034454 | -0.032672
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455 | -0.050838 | -0.036251 | -0.034365 | -0.032573
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48358 | 4.8685 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136 | -0.051901 | -0.035962 | -0.034314 | -0.032741
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652 | -0.04122 | -0.036214 | -0.03445 | -0.032672
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273 | -0.042969 | -0.036214 | -0.034432 | -0.032624
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239 | -0.044272 | -0.036107 | -0.034449 | -0.032607
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435 | -0.046021 | -0.036162 | -0.034347 | -0.032622
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791 | -0.047284 | -0.03614 | -0.034314 | -0.032738
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265 | -0.048523 | -0.036125 | -0.034469 | -0.032525
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826 | -0.049696 | -0.036107 | -0.034454 | -0.032672
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455 | -0.050838 | -0.036251 | -0.034365 | -0.032573
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48319 | 4.8665 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136 | -0.051901 | -0.035962 | -0.034314 | -0.032741
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.03 | 2204 | 8276 | 8681 | 9106 | -0.039233 | -0.034418 | -0.032865 | -0.031174
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.035 | 2092 | 7093 | 7441 | 7805 | -0.040807 | -0.034572 | -0.032757 | -0.031157
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.04 | 1987 | 6207 | 6511 | 6829 | -0.04241 | -0.034381 | -0.032828 | -0.03121
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.045 | 1890 | 5517 | 5787 | 6071 | -0.044006 | -0.034477 | -0.032921 | -0.03112
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.05 | 1800 | 4965 | 5208 | 5463 | -0.045093 | -0.03461 | -0.032869 | -0.031211
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.055 | 1716 | 4514 | 4735 | 4967 | -0.046667 | -0.034439 | -0.032884 | -0.031207
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.06 | 1638 | 4138 | 4340 | 4553 | -0.047674 | -0.034531 | -0.032977 | -0.031277
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.065 | 1565 | 3819 | 4006 | 4203 | -0.048632 | -0.034631 | -0.033068 | -0.03112
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.48237 | 4.7785 | 199.872 | 0.07 | 1497 | 3547 | 3720 | 3902 | -0.049524 | -0.034304 | -0.033013 | -0.031281
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.03 | 1969 | 7490 | 7896 | 8324 | -0.040916 | -0.036656 | -0.034837 | -0.032993
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.035 | 1860 | 6420 | 6768 | 7135 | -0.042717 | -0.036615 | -0.034797 | -0.032936
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.04 | 1760 | 5617 | 5922 | 6243 | -0.043998 | -0.0367 | -0.034876 | -0.032993
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.045 | 1667 | 4993 | 5264 | 5549 | -0.045793 | -0.036658 | -0.034837 | -0.033107
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.05 | 1581 | 4494 | 4738 | 4995 | -0.047016 | -0.036656 | -0.034637 | -0.032914
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.055 | 1502 | 4085 | 4307 | 4540 | -0.048162 | -0.036784 | -0.034738 | -0.033014
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.06 | 1429 | 3745 | 3948 | 4162 | -0.049235 | -0.036532 | -0.034719 | -0.032993
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.065 | 1361 | 3457 | 3644 | 3842 | -0.050244 | -0.036511 | -0.034958 | -0.032973
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.48235 | 5.2814 | 199.872 | 0.07 | 1298 | 3210 | 3384 | 3568 | -0.05117 | -0.036615 | -0.034797 | -0.0328
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.03 | 1969 | 7490 | 7896 | 8324 | -0.040916 | -0.036656 | -0.034837 | -0.032993
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.035 | 1860 | 6420 | 6768 | 7135 | -0.042717 | -0.036615 | -0.034797 | -0.032936
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.04 | 1760 | 5617 | 5922 | 6243 | -0.043998 | -0.0367 | -0.034876 | -0.032993
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.045 | 1667 | 4993 | 5264 | 5549 | -0.045793 | -0.036658 | -0.034837 | -0.033107
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.05 | 1581 | 4494 | 4738 | 4995 | -0.047016 | -0.036656 | -0.034637 | -0.032914
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.055 | 1502 | 4085 | 4307 | 4540 | -0.048162 | -0.036784 | -0.034738 | -0.033014
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.06 | 1429 | 3745 | 3948 | 4162 | -0.049235 | -0.036532 | -0.034719 | -0.032993
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.065 | 1361 | 3457 | 3644 | 3842 | -0.050244 | -0.036511 | -0.034958 | -0.032973
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.48257 | 5.2826 | 199.872 | 0.07 | 1298 | 3210 | 3384 | 3568 | -0.05117 | -0.036615 | -0.034797 | -0.0328
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.03 | 1969 | 7490 | 7896 | 8324 | -0.039043 | -0.034669 | -0.032945 | -0.031305
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.035 | 1860 | 6420 | 6768 | 7135 | -0.040743 | -0.034732 | -0.033005 | -0.031229
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.04 | 1760 | 5617 | 5922 | 6243 | -0.041916 | -0.03488 | -0.032985 | -0.031192
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.045 | 1667 | 4993 | 5264 | 5549 | -0.043054 | -0.034796 | -0.033064 | -0.03125
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.05 | 1581 | 4494 | 4738 | 4995 | -0.044713 | -0.034794 | -0.032864 | -0.031226
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.055 | 1502 | 4085 | 4307 | 4540 | -0.045743 | -0.034735 | -0.033004 | -0.031363
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.06 | 1429 | 3745 | 3948 | 4162 | -0.046698 | -0.034794 | -0.033064 | -0.031192
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.065 | 1361 | 3457 | 3644 | 3842 | -0.047586 | -0.034627 | -0.033165 | -0.031266
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.48248 | 5.2821 | 199.872 | 0.07 | 1298 | 3210 | 3384 | 3568 | -0.048387 | -0.034586 | -0.032867 | -0.031225
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.03 | 1969 | 7490 | 7896 | 8324 | -0.039043 | -0.034669 | -0.032945 | -0.031305
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.035 | 1860 | 6420 | 6768 | 7135 | -0.040743 | -0.034732 | -0.033005 | -0.031229
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.04 | 1760 | 5617 | 5922 | 6243 | -0.041916 | -0.03488 | -0.032985 | -0.031192
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.045 | 1667 | 4993 | 5264 | 5549 | -0.043054 | -0.034796 | -0.033064 | -0.03125
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.05 | 1581 | 4494 | 4738 | 4995 | -0.044713 | -0.034794 | -0.032864 | -0.031226
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.055 | 1502 | 4085 | 4307 | 4540 | -0.045743 | -0.034735 | -0.033004 | -0.031363
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.06 | 1429 | 3745 | 3948 | 4162 | -0.046698 | -0.034794 | -0.033064 | -0.031192
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.065 | 1361 | 3457 | 3644 | 3842 | -0.047586 | -0.034627 | -0.033165 | -0.031266
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.48247 | 5.282 | 199.872 | 0.07 | 1298 | 3210 | 3384 | 3568 | -0.048387 | -0.034586 | -0.032867 | -0.031225
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.03 | 1882 | 7139 | 7517 | 7916 | -0.039306 | -0.035009 | -0.033432 | -0.031682
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.035 | 1779 | 6119 | 6444 | 6785 | -0.04097 | -0.03501 | -0.033303 | -0.031683
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.04 | 1685 | 5354 | 5638 | 5937 | -0.042614 | -0.035141 | -0.03343 | -0.031642
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.045 | 1597 | 4759 | 5012 | 5278 | -0.044285 | -0.035077 | -0.033365 | -0.03156
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.05 | 1517 | 4283 | 4510 | 4750 | -0.04471 | -0.035143 | -0.033433 | -0.0316
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.055 | 1442 | 3894 | 4100 | 4318 | -0.046296 | -0.034944 | -0.033475 | -0.031621
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.06 | 1372 | 3569 | 3759 | 3958 | -0.047883 | -0.035145 | -0.033179 | -0.031563
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.065 | 1308 | 3295 | 3470 | 3654 | -0.048727 | -0.035139 | -0.033157 | -0.03154
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.48479 | 5.1707 | 214.272 | 0.07 | 1248 | 3059 | 3222 | 3393 | -0.049505 | -0.03532 | -0.033303 | -0.031402
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.03 | 1674 | 6424 | 6802 | 7202 | -0.040688 | -0.037026 | -0.035177 | -0.033289
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.035 | 1575 | 5506 | 5830 | 6173 | -0.042553 | -0.037076 | -0.035247 | -0.033203
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.04 | 1485 | 4818 | 5101 | 5402 | -0.043786 | -0.036978 | -0.035181 | -0.033113
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.045 | 1402 | 4282 | 4535 | 4801 | -0.044959 | -0.037104 | -0.035106 | -0.033226
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.05 | 1325 | 3854 | 4081 | 4321 | -0.046763 | -0.037222 | -0.035225 | -0.033333
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.055 | 1255 | 3504 | 3710 | 3928 | -0.048522 | -0.037098 | -0.035111 | -0.033227
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.06 | 1191 | 3212 | 3401 | 3601 | -0.048722 | -0.03717 | -0.035177 | -0.033289
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.065 | 1131 | 2965 | 3139 | 3324 | -0.050378 | -0.037025 | -0.035341 | -0.033159
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.48543 | 5.7187 | 214.272 | 0.07 | 1076 | 2753 | 2915 | 3087 | -0.051146 | -0.037076 | -0.035088 | -0.033198
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.03 | 1674 | 6424 | 6802 | 7202 | -0.040688 | -0.037026 | -0.035177 | -0.033289
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.035 | 1575 | 5506 | 5830 | 6173 | -0.042553 | -0.037076 | -0.035247 | -0.033203
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.04 | 1485 | 4818 | 5101 | 5402 | -0.043786 | -0.036978 | -0.035181 | -0.033113
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.045 | 1402 | 4282 | 4535 | 4801 | -0.044959 | -0.037104 | -0.035106 | -0.033226
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.05 | 1325 | 3854 | 4081 | 4321 | -0.046763 | -0.037222 | -0.035225 | -0.033333
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.055 | 1255 | 3504 | 3710 | 3928 | -0.048522 | -0.037098 | -0.035111 | -0.033227
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.06 | 1191 | 3212 | 3401 | 3601 | -0.048722 | -0.03717 | -0.035177 | -0.033289
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.065 | 1131 | 2965 | 3139 | 3324 | -0.050378 | -0.037025 | -0.035341 | -0.033159
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.48617 | 5.7231 | 214.272 | 0.07 | 1076 | 2753 | 2915 | 3087 | -0.051146 | -0.037076 | -0.035088 | -0.033198
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.03 | 1671 | 6412 | 6790 | 7190 | -0.040758 | -0.036948 | -0.0351 | -0.033212
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.035 | 1572 | 5496 | 5820 | 6163 | -0.042048 | -0.036972 | -0.035146 | -0.033255
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.04 | 1482 | 4809 | 5092 | 5393 | -0.043871 | -0.037044 | -0.035241 | -0.033166
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.045 | 1399 | 4274 | 4526 | 4793 | -0.045051 | -0.037171 | -0.035174 | -0.03328
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.05 | 1322 | 3847 | 4074 | 4314 | -0.046864 | -0.037046 | -0.035054 | -0.033169
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.055 | 1252 | 3497 | 3703 | 3922 | -0.047909 | -0.03717 | -0.035175 | -0.033276
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.06 | 1188 | 3206 | 3395 | 3595 | -0.048839 | -0.036948 | -0.034963 | -0.033342
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.065 | 1128 | 2959 | 3134 | 3319 | -0.050505 | -0.037097 | -0.035099 | -0.032925
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.48706 | 5.7283 | 214.272 | 0.07 | 1073 | 2748 | 2910 | 3081 | -0.051282 | -0.037141 | -0.035146 | -0.03326
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.03 | 1668 | 6400 | 6778 | 7178 | -0.04248 | -0.03875 | -0.036805 | -0.034826
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.035 | 1569 | 5485 | 5809 | 6153 | -0.043876 | -0.0389 | -0.036969 | -0.034824
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.04 | 1478 | 4800 | 5083 | 5384 | -0.046452 | -0.038847 | -0.036946 | -0.034779
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.045 | 1395 | 4266 | 4518 | 4785 | -0.047782 | -0.038973 | -0.036879 | -0.034893
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.05 | 1319 | 3840 | 4067 | 4307 | -0.049027 | -0.038798 | -0.036712 | -0.034738
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.055 | 1249 | 3491 | 3697 | 3915 | -0.05019 | -0.038822 | -0.036738 | -0.035001
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.06 | 1185 | 3200 | 3389 | 3589 | -0.051241 | -0.03875 | -0.036669 | -0.034956
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.065 | 1125 | 2954 | 3128 | 3313 | -0.05303 | -0.038724 | -0.036946 | -0.034674
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.48824 | 5.7353 | 214.272 | 0.07 | 1070 | 2743 | 2905 | 3076 | -0.053935 | -0.038893 | -0.036804 | -0.034829
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.03 | 1602 | 6134 | 6488 | 6863 | -0.040719 | -0.037351 | -0.035528 | -0.033516
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.035 | 1508 | 5257 | 5561 | 5883 | -0.043147 | -0.037532 | -0.035553 | -0.033514
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.04 | 1423 | 4600 | 4866 | 5147 | -0.044325 | -0.037456 | -0.035481 | -0.033609
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.045 | 1344 | 4089 | 4325 | 4575 | -0.046132 | -0.037429 | -0.035459 | -0.033587
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.05 | 1272 | 3680 | 3893 | 4118 | -0.047191 | -0.037405 | -0.035431 | -0.03356
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.055 | 1205 | 3346 | 3539 | 3744 | -0.048934 | -0.037399 | -0.035432 | -0.033308
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.06 | 1144 | 3067 | 3244 | 3432 | -0.049834 | -0.037351 | -0.035385 | -0.033512
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.065 | 1087 | 2831 | 2994 | 3168 | -0.051483 | -0.037402 | -0.035749 | -0.033557
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.49713 | 5.6212 | 228.672 | 0.07 | 1035 | 2629 | 2781 | 2941 | -0.052198 | -0.037349 | -0.03538 | -0.03352
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.03 | 1418 | 5248 | 5833 | 6208 | -0.041892 | -0.07849 | -0.037141 | -0.034976
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.035 | 1329 | 4513 | 5000 | 5321 | -0.043197 | -0.075394 | -0.03698 | -0.035002
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.04 | 1247 | 3960 | 4375 | 4656 | -0.045176 | -0.073034 | -0.03698 | -0.035026
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.045 | 1173 | 3529 | 3889 | 4139 | -0.046341 | -0.070827 | -0.036899 | -0.034973
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.05 | 1105 | 3182 | 3500 | 3725 | -0.048234 | -0.069046 | -0.037139 | -0.034974
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.055 | 1043 | 2898 | 3182 | 3386 | -0.049225 | -0.067267 | -0.036925 | -0.035053
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.06 | 986 | 2660 | 2917 | 3104 | -0.051011 | -0.066011 | -0.036976 | -0.034826
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.065 | 934 | 2460 | 2692 | 2865 | -0.051777 | -0.064639 | -0.037196 | -0.035029
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.49969 | 6.2288 | 228.672 | 0.07 | 886 | 2286 | 2500 | 2661 | -0.053419 | -0.063882 | -0.03698 | -0.03482
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.03 | 1413 | 5207 | 5813 | 6188 | -0.041384 | -0.079059 | -0.037105 | -0.034934
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.035 | 1323 | 4479 | 4983 | 5304 | -0.044075 | -0.076114 | -0.036915 | -0.034934
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.04 | 1242 | 3932 | 4360 | 4641 | -0.04535 | -0.073297 | -0.037102 | -0.034934
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.045 | 1168 | 3504 | 3876 | 4125 | -0.046531 | -0.071296 | -0.036779 | -0.035088
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.05 | 1100 | 3161 | 3488 | 3713 | -0.048443 | -0.069473 | -0.036996 | -0.034832
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.055 | 1038 | 2879 | 3171 | 3375 | -0.049451 | -0.067681 | -0.037048 | -0.034887
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.06 | 982 | 2643 | 2907 | 3094 | -0.05029 | -0.066408 | -0.036779 | -0.034934
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.065 | 930 | 2444 | 2683 | 2856 | -0.051988 | -0.065392 | -0.036971 | -0.034809
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.5027 | 6.2476 | 228.672 | 0.07 | 882 | 2272 | 2491 | 2652 | -0.052632 | -0.06425 | -0.037109 | -0.034934
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.03 | 1407 | 5166 | 5794 | 6168 | -0.042206 | -0.079637 | -0.036902 | -0.034893
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.035 | 1318 | 4445 | 4966 | 5287 | -0.043541 | -0.076651 | -0.03685 | -0.034867
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.04 | 1237 | 3903 | 4345 | 4626 | -0.044788 | -0.074021 | -0.037012 | -0.034842
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.045 | 1163 | 3480 | 3862 | 4112 | -0.046721 | -0.071752 | -0.037148 | -0.034968
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.05 | 1095 | 3140 | 3476 | 3701 | -0.048653 | -0.06963 | -0.037119 | -0.034941
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.055 | 1033 | 2860 | 3160 | 3365 | -0.049678 | -0.0681 | -0.036879 | -0.03471
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.06 | 977 | 2626 | 2897 | 3084 | -0.050534 | -0.066809 | -0.036902 | -0.035044
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.065 | 925 | 2428 | 2674 | 2847 | -0.052254 | -0.065795 | -0.03709 | -0.034915
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.50587 | 6.2673 | 228.672 | 0.07 | 878 | 2257 | 2483 | 2644 | -0.052859 | -0.065037 | -0.03685 | -0.034684
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.03 | 1402 | 5126 | 5774 | 6149 | -0.041695 | -0.080208 | -0.036864 | -0.034694
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.035 | 1313 | 4412 | 4949 | 5270 | -0.043003 | -0.077181 | -0.036972 | -0.034799
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.04 | 1232 | 3875 | 4330 | 4612 | -0.044961 | -0.074516 | -0.036922 | -0.034743
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.045 | 1158 | 3455 | 3849 | 4099 | -0.046129 | -0.072234 | -0.037028 | -0.034848
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.05 | 1090 | 3118 | 3464 | 3689 | -0.048035 | -0.070364 | -0.036975 | -0.034799
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.055 | 1029 | 2841 | 3149 | 3354 | -0.048983 | -0.068525 | -0.037003 | -0.03482
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.06 | 972 | 2609 | 2887 | 3074 | -0.050781 | -0.067215 | -0.037025 | -0.034851
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.065 | 921 | 2413 | 2665 | 2838 | -0.051493 | -0.066176 | -0.036863 | -0.034694
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.50968 | 6.2908 | 228.672 | 0.07 | 873 | 2243 | 2475 | 2635 | -0.053145 | -0.065027 | -0.03659 | -0.034799
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.03 | 1339 | 4975 | 5506 | 5859 | -0.042203 | -0.076309 | -0.037244 | -0.035079
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.035 | 1255 | 4277 | 4720 | 5022 | -0.043445 | -0.073641 | -0.037128 | -0.034973
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.04 | 1178 | 3752 | 4130 | 4394 | -0.045381 | -0.071287 | -0.037072 | -0.035134
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.045 | 1108 | 3342 | 3671 | 3906 | -0.047291 | -0.06934 | -0.036988 | -0.035079
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.05 | 1044 | 3014 | 3304 | 3515 | -0.048314 | -0.06745 | -0.037015 | -0.035136
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.055 | 986 | 2745 | 3003 | 3196 | -0.04918 | -0.065691 | -0.037191 | -0.035024
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.06 | 932 | 2519 | 2753 | 2930 | -0.050916 | -0.064612 | -0.037076 | -0.034914
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.065 | 883 | 2328 | 2541 | 2704 | -0.052575 | -0.063556 | -0.037135 | -0.034975
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.53133 | 6.2095 | 243.072 | 0.07 | 838 | 2164 | 2360 | 2511 | -0.053107 | -0.062392 | -0.037128 | -0.034973
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.03 | 1176 | 3637 | 4901 | 5252 | -0.042345 | -0.11184 | -0.038643 | -0.036153
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.035 | 1096 | 3173 | 4201 | 4502 | -0.044464 | -0.10645 | -0.038453 | -0.036181
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.04 | 1023 | 2819 | 3676 | 3939 | -0.046598 | -0.10194 | -0.038451 | -0.036212
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.045 | 958 | 2537 | 3267 | 3501 | -0.047714 | -0.098116 | -0.038552 | -0.036334
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.05 | 898 | 2308 | 2941 | 3151 | -0.049735 | -0.094902 | -0.038575 | -0.036097
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.055 | 845 | 2118 | 2673 | 2865 | -0.049494 | -0.092156 | -0.038489 | -0.036003
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.06 | 796 | 1956 | 2451 | 2626 | -0.051251 | -0.089809 | -0.038446 | -0.03633
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.065 | 751 | 1817 | 2262 | 2424 | -0.052963 | -0.087851 | -0.038674 | -0.036183
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.53901 | 6.9125 | 243.072 | 0.07 | 710 | 1697 | 2101 | 2251 | -0.054594 | -0.08616 | -0.038444 | -0.035974
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.03 | 1164 | 3522 | 4854 | 5204 | -0.041975 | -0.1153 | -0.038241 | -0.036118
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.035 | 1084 | 3078 | 4160 | 4461 | -0.044092 | -0.10963 | -0.038373 | -0.036085
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.04 | 1012 | 2739 | 3640 | 3903 | -0.045283 | -0.10461 | -0.038563 | -0.036058
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.045 | 946 | 2468 | 3236 | 3469 | -0.047331 | -0.10058 | -0.038336 | -0.036121
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.05 | 887 | 2248 | 2912 | 3123 | -0.049303 | -0.097189 | -0.038309 | -0.035814
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.055 | 834 | 2064 | 2648 | 2839 | -0.050114 | -0.09434 | -0.03814 | -0.035993
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.06 | 785 | 1908 | 2427 | 2602 | -0.051932 | -0.091861 | -0.038431 | -0.035939
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.065 | 741 | 1773 | 2240 | 2402 | -0.05243 | -0.089836 | -0.038627 | -0.036116
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.54869 | 6.9743 | 243.072 | 0.07 | 701 | 1657 | 2080 | 2230 | -0.052703 | -0.088057 | -0.038373 | -0.036301
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.03 | 1148 | 3369 | 4753 | 5142 | -0.041736 | -0.11991 | -0.045965 | -0.035815
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.035 | 1068 | 2952 | 4078 | 4407 | -0.043868 | -0.11378 | -0.044965 | -0.035878
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.04 | 996 | 2632 | 3571 | 3856 | -0.045062 | -0.1084 | -0.044165 | -0.036
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.045 | 931 | 2376 | 3176 | 3428 | -0.047083 | -0.10407 | -0.043662 | -0.035724
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.05 | 873 | 2167 | 2860 | 3085 | -0.047983 | -0.10046 | -0.043158 | -0.035937
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.055 | 820 | 1992 | 2602 | 2804 | -0.049826 | -0.097417 | -0.042326 | -0.036095
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.06 | 772 | 1843 | 2385 | 2571 | -0.050431 | -0.094794 | -0.042553 | -0.035634
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.065 | 728 | 1715 | 2202 | 2373 | -0.052083 | -0.092593 | -0.042192 | -0.035758
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.56032 | 7.0479 | 243.072 | 0.07 | 688 | 1603 | 2046 | 2204 | -0.053645 | -0.090754 | -0.041686 | -0.035449
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.03 | 1130 | 3197 | 4615 | 5072 | -0.039116 | -0.12098 | -0.058355 | -0.034273
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.035 | 1050 | 2810 | 3966 | 4348 | -0.041971 | -0.1144 | -0.055939 | -0.034207
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.04 | 979 | 2512 | 3478 | 3804 | -0.043011 | -0.1089 | -0.053863 | -0.034273
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.045 | 915 | 2272 | 3097 | 3382 | -0.044885 | -0.10445 | -0.052036 | -0.03399
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.05 | 857 | 2076 | 2791 | 3043 | -0.045657 | -0.10052 | -0.051003 | -0.034275
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.055 | 805 | 1912 | 2542 | 2767 | -0.047337 | -0.097262 | -0.049009 | -0.034206
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.06 | 757 | 1771 | 2332 | 2536 | -0.048995 | -0.094581 | -0.048552 | -0.034273
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.065 | 714 | 1649 | 2155 | 2341 | -0.049268 | -0.09246 | -0.047303 | -0.034241
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.57541 | 7.1421 | 243.072 | 0.07 | 675 | 1543 | 2003 | 2174 | -0.049296 | -0.090748 | -0.046644 | -0.034207
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.03 | 1066 | 3018 | 4357 | 4789 | -0.030027 | -0.092331 | -0.049105 | -0.025239
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.035 | 992 | 2654 | 3744 | 4105 | -0.030303 | -0.087031 | -0.046843 | -0.025172
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.04 | 924 | 2372 | 3283 | 3592 | -0.032461 | -0.082753 | -0.044807 | -0.025237
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.045 | 864 | 2146 | 2924 | 3192 | -0.032475 | -0.079365 | -0.042881 | -0.025344
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.05 | 809 | 1960 | 2635 | 2873 | -0.034606 | -0.076343 | -0.04147 | -0.025441
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.055 | 760 | 1805 | 2399 | 2612 | -0.034307 | -0.073409 | -0.040016 | -0.025373
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.06 | 715 | 1672 | 2202 | 2394 | -0.035088 | -0.071627 | -0.038848 | -0.025641
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.065 | 674 | 1558 | 2035 | 2210 | -0.037143 | -0.069851 | -0.037825 | -0.025573
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62122 | 7.1448 | 257.472 | 0.07 | 637 | 1457 | 1890 | 2052 | -0.037764 | -0.068414 | -0.037678 | -0.025641
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.03 | 918 | 1457 | 3052 | 4175 | -0.023404 | -0.12492 | -0.066667 | -0.026807
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.035 | 848 | 1364 | 2686 | 3582 | -0.024166 | -0.11256 | -0.061495 | -0.025836
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.04 | 785 | 1280 | 2402 | 3136 | -0.026055 | -0.10301 | -0.05767 | -0.025482
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.045 | 730 | 1203 | 2175 | 2789 | -0.026667 | -0.096168 | -0.054348 | -0.024825
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.05 | 680 | 1134 | 1989 | 2512 | -0.027182 | -0.089888 | -0.051502 | -0.024087
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.055 | 635 | 1070 | 1832 | 2285 | -0.029052 | -0.08547 | -0.048806 | -0.023504
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.06 | 595 | 1011 | 1698 | 2096 | -0.029364 | -0.082577 | -0.047138 | -0.022844
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.065 | 559 | 957 | 1583 | 1935 | -0.029514 | -0.080692 | -0.045235 | -0.022727
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.64341 | 8.0367 | 257.472 | 0.07 | 527 | 908 | 1481 | 1797 | -0.029466 | -0.077236 | -0.043899 | -0.022838
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.03 | 909 | 1444 | 2965 | 4104 | -0.020474 | -0.05 | -0.059924 | -0.032304
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.035 | 839 | 1352 | 2615 | 3526 | -0.022145 | -0.046544 | -0.055275 | -0.029986
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.04 | 777 | 1268 | 2344 | 3090 | -0.022642 | -0.044461 | -0.051396 | -0.028607
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.045 | 722 | 1191 | 2125 | 2751 | -0.023004 | -0.043373 | -0.048365 | -0.027228
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.05 | 672 | 1122 | 1946 | 2480 | -0.024673 | -0.041026 | -0.045611 | -0.02554
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.055 | 628 | 1058 | 1794 | 2257 | -0.024845 | -0.039927 | -0.04371 | -0.024211
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.06 | 588 | 1000 | 1665 | 2071 | -0.02649 | -0.039385 | -0.041451 | -0.023574
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.065 | 553 | 947 | 1553 | 1913 | -0.024691 | -0.039554 | -0.040173 | -0.022983
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.65285 | 8.0955 | 257.472 | 0.07 | 520 | 898 | 1454 | 1778 | -0.026217 | -0.038544 | -0.038995 | -0.022002
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.03 | 908 | 1442 | 2951 | 4092 | -0.018378 | -0.028302 | -0.055378 | -0.032395
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.035 | 838 | 1350 | 2604 | 3516 | -0.019883 | -0.027378 | -0.051366 | -0.030069
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.04 | 776 | 1266 | 2334 | 3082 | -0.020202 | -0.02765 | -0.047736 | -0.028373
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.045 | 721 | 1189 | 2117 | 2745 | -0.02038 | -0.0278 | -0.045106 | -0.026596
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.05 | 671 | 1120 | 1938 | 2474 | -0.021866 | -0.026933 | -0.042963 | -0.025217
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.055 | 627 | 1056 | 1788 | 2253 | -0.021841 | -0.026728 | -0.040258 | -0.023407
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.06 | 587 | 998 | 1659 | 2067 | -0.023295 | -0.02729 | -0.038818 | -0.022695
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.065 | 552 | 945 | 1548 | 1910 | -0.023009 | -0.027778 | -0.037313 | -0.021516
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.65552 | 8.112 | 257.472 | 0.07 | 519 | 896 | 1450 | 1775 | -0.024436 | -0.027144 | -0.035904 | -0.02096
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.03 | 905 | 1438 | 2921 | 4068 | -0.018438 | -0.01776 | -0.056525 | -0.033959
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.035 | 835 | 1345 | 2580 | 3497 | -0.019953 | -0.018964 | -0.051819 | -0.03157
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.04 | 773 | 1262 | 2314 | 3067 | -0.020279 | -0.018663 | -0.04852 | -0.029123
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.045 | 718 | 1186 | 2100 | 2732 | -0.021798 | -0.019835 | -0.045455 | -0.027412
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.05 | 669 | 1116 | 1924 | 2463 | -0.02193 | -0.020193 | -0.042786 | -0.026097
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.055 | 625 | 1053 | 1775 | 2243 | -0.021909 | -0.020465 | -0.041059 | -0.024358
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.06 | 585 | 995 | 1648 | 2059 | -0.023372 | -0.021632 | -0.039067 | -0.023245
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.065 | 549 | 942 | 1538 | 1902 | -0.024867 | -0.021807 | -0.037547 | -0.022108
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.65875 | 8.132 | 257.472 | 0.07 | 517 | 893 | 1440 | 1768 | -0.024528 | -0.021906 | -0.036789 | -0.021583
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.03 | 890 | 1576 | 3097 | 4063 | -0.019824 | -0.1151 | -0.050291 | -0.017175
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.035 | 823 | 1455 | 2711 | 3483 | -0.020238 | -0.10406 | -0.046765 | -0.016935
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.04 | 763 | 1351 | 2414 | 3047 | -0.021795 | -0.095716 | -0.04396 | -0.017097
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.045 | 710 | 1260 | 2178 | 2709 | -0.022039 | -0.089595 | -0.041795 | -0.017054
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.05 | 662 | 1180 | 1985 | 2438 | -0.022157 | -0.083851 | -0.039671 | -0.016935
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.055 | 619 | 1108 | 1825 | 2216 | -0.023659 | -0.079734 | -0.037447 | -0.017295
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.06 | 581 | 1044 | 1688 | 2031 | -0.023529 | -0.076106 | -0.035979 | -0.017417
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.065 | 546 | 985 | 1570 | 1875 | -0.023256 | -0.073377 | -0.035034 | -0.017296
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.67426 | 7.8923 | 271.872 | 0.07 | 514 | 933 | 1468 | 1741 | -0.024668 | -0.070717 | -0.034211 | -0.017494
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.03 | 777 | 1243 | 1902 | 3143 | -0.020177 | -0.018167 | -0.085577 | -0.044681
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.035 | 714 | 1159 | 1741 | 2749 | -0.020576 | -0.018628 | -0.076882 | -0.040489
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.04 | 659 | 1083 | 1607 | 2446 | -0.020802 | -0.01991 | -0.070023 | -0.037387
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.045 | 609 | 1014 | 1493 | 2205 | -0.022472 | -0.02029 | -0.06395 | -0.034588
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.05 | 566 | 951 | 1393 | 2009 | -0.022453 | -0.021605 | -0.060054 | -0.032274
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.055 | 527 | 895 | 1305 | 1846 | -0.022263 | -0.021858 | -0.056399 | -0.029953
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.06 | 492 | 843 | 1227 | 1707 | -0.02381 | -0.022042 | -0.053241 | -0.028458
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.065 | 461 | 796 | 1157 | 1588 | -0.02537 | -0.023313 | -0.050861 | -0.026961
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.6804 | 8.7626 | 271.872 | 0.07 | 434 | 753 | 1093 | 1484 | -0.022523 | -0.023346 | -0.048738 | -0.025607
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.03 | 771 | 1235 | 1833 | 3087 | -0.02033 | -0.017502 | -0.088966 | -0.045455
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.035 | 709 | 1151 | 1686 | 2704 | -0.019364 | -0.018755 | -0.078689 | -0.041135
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.04 | 653 | 1075 | 1561 | 2410 | -0.02099 | -0.019161 | -0.071938 | -0.03754
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.045 | 604 | 1006 | 1454 | 2175 | -0.022654 | -0.020448 | -0.065553 | -0.035049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.05 | 561 | 944 | 1359 | 1984 | -0.022648 | -0.020747 | -0.061464 | -0.032195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.055 | 522 | 887 | 1275 | 1824 | -0.024299 | -0.022051 | -0.05765 | -0.030303
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.06 | 488 | 836 | 1201 | 1688 | -0.024 | -0.022222 | -0.053586 | -0.028769
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.065 | 457 | 789 | 1133 | 1571 | -0.023504 | -0.022305 | -0.051883 | -0.027245
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.68841 | 8.8141 | 271.872 | 0.07 | 429 | 747 | 1072 | 1469 | -0.025 | -0.022251 | -0.049645 | -0.025862
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.03 | 763 | 1223 | 1737 | 3008 | -0.01928 | -0.017671 | -0.09295 | -0.046593
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.035 | 701 | 1139 | 1608 | 2641 | -0.01958 | -0.018949 | -0.082192 | -0.042422
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.04 | 646 | 1063 | 1496 | 2358 | -0.021212 | -0.019373 | -0.07483 | -0.038728
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.045 | 597 | 995 | 1398 | 2133 | -0.021311 | -0.019704 | -0.068621 | -0.035714
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.05 | 554 | 933 | 1312 | 1948 | -0.022928 | -0.020986 | -0.062857 | -0.032771
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.055 | 516 | 877 | 1234 | 1793 | -0.022727 | -0.021205 | -0.058734 | -0.030811
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.06 | 482 | 826 | 1164 | 1661 | -0.022312 | -0.022485 | -0.055195 | -0.029223
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.065 | 451 | 780 | 1100 | 1547 | -0.02381 | -0.022556 | -0.053356 | -0.027656
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.69799 | 8.8752 | 271.872 | 0.07 | 424 | 737 | 1042 | 1447 | -0.023041 | -0.023841 | -0.051002 | -0.0269
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.03 | 756 | 1211 | 1641 | 2929 | -0.016905 | -0.016247 | -0.090859 | -0.044372
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.035 | 693 | 1127 | 1530 | 2579 | -0.018414 | -0.017437 | -0.079976 | -0.039836
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.04 | 639 | 1052 | 1431 | 2307 | -0.018433 | -0.01774 | -0.072586 | -0.036743
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.045 | 590 | 984 | 1343 | 2090 | -0.019934 | -0.018943 | -0.066064 | -0.033749
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.05 | 547 | 923 | 1264 | 1912 | -0.021467 | -0.019129 | -0.060921 | -0.030917
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.055 | 510 | 867 | 1192 | 1762 | -0.019231 | -0.019231 | -0.056215 | -0.029201
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.06 | 476 | 816 | 1126 | 1634 | -0.020576 | -0.020408 | -0.053782 | -0.027381
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.065 | 446 | 770 | 1067 | 1523 | -0.01978 | -0.021601 | -0.050712 | -0.026215
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.71047 | 8.9542 | 271.872 | 0.07 | 418 | 728 | 1012 | 1426 | -0.023364 | -0.021505 | -0.047977 | -0.02529