## Slab_Properties
Slab properties: |  |  | bay type
l1 = | 36 | ft | exterior | * must be larger span
l2 = | 32 | ft | interior
l1 / l2 = |  |  | * must be < 2.0
c1 = | 24 | in
c2 = | 24 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = |  | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 15 | in
d = |  | in
wc = | 150 | pcf
yt = |  | in
n =
lcw = |  |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = |  | psi
Strip widths
Direction | Column | Middle
l1 |  |  | ft | *per ACI 318-14,
l2 |  |  | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = |  | psf
mass = |  | lb sec2/ft
weight = |  | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = |  |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = |  | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = |  | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = |  | k-ft
M1n1u = |  | k-ft
M1n2u = |  | k-ft
M2pu = |  | k-ft
M2n1u = |  | k-ft
M2n2u = |  | k-ft
Service Moments
M01,DL = |  | k-ft | *includes SDL and self-weight
M01,LL = |  | k-ft
M02,DL = |  | k-ft
M02,LL = |  | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p |  |  | k-ft
l1 | DL | n1 |  |  | k-ft
l1 | DL | n2 |  |  | k-ft
l1 | LL | p |  |  | k-ft
l1 | LL | n1 |  |  | k-ft
l1 | LL | n2 |  |  | k-ft
l2 | DL | p |  |  | k-ft
l2 | DL | n1 |  |  | k-ft
l2 | DL | n2 |  |  | k-ft
l2 | LL | p |  |  | k-ft
l2 | LL | n1 |  |  | k-ft
l2 | LL | n2 |  |  | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p |  |  | k-ft
l1 | n1 |  |  | k-ft
l1 | n2 |  |  | k-ft
l2 | p |  |  | k-ft
l2 | n1 |  |  | k-ft
l2 | n2 |  |  | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation: |  |  |  |  | User input:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Column | Middle
l1 | p |  |  | in2 | l1 | p |  |  | in2
l1 | n1 |  |  | in2 | l1 | n1 |  |  | in2
l1 | n2 |  |  | in2 | l1 | n2 |  |  | in2
l2 | p |  |  | in2 | l2 | p |  |  | in2
l2 | n1 |  |  | in2 | l2 | n1 |  |  | in2
l2 | n2 |  |  | in2 | l2 | n2 |  |  | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p |  |  | in3
l1 | n1 |  |  | in3
l1 | n2 |  |  | in3
l2 | p |  |  | in3
l2 | n1 |  |  | in3
l2 | n2 |  |  | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p |  |  | in3
l1 | n1 |  |  | in3
l1 | n2 |  |  | in3
l2 | p |  |  | in3
l2 | n1 |  |  | in3
l2 | n2 |  |  | in3
Calculate avg strip Ie
Direction | Column | Middle
l1 |  |  | in3
l2 |  |  | in3
Calculate Panel Ie
Iep = |  | in3
Calculate Panel Ig
Igp = |  | in3
Calculate k1
k1 =
Calculate fi |  |  | Interp li2
k2 = |  |  | 1 | 7.12
li2 = |  |  | 1.5 | 8.92
g = |  | slug / ft2 | 2 | 9.29
fi = |  | Hz
Calculate/Input Parameters for DG11
W = |  | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits
fn= |  | Hz
W = |  | lb
b =
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips
Very Slow |  | 1.25 | [9 empty] | mips
Slow |  | 1.6 | 6.8 | 6 | 8 | 0.1 | [5 empty] | mips | * does not consider mode scaling
Moderate |  | 1.85 | 8 | 7 | 9 | 0.09 | [5 empty] | mips
Fast |  | 2.1 | 8.8 | 8 | 10 | 0.08 | [5 empty] | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194

## thickness_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11

## thickness_study
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.025 | 5155 | 20346 | 20918 | 21505
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.03 | 4990 | 16955 | 17432 | 17921
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.035 | 4832 | 14533 | 14941 | 15361
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.04 | 4681 | 12717 | 13074 | 13441
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.045 | 4536 | 11304 | 11621 | 11947
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.05 | 4398 | 10173 | 10459 | 10753
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.055 | 4265 | 9248 | 9508 | 9775
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.06 | 4138 | 8478 | 8716 | 8961
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.065 | 4016 | 7826 | 8045 | 8271
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00412 | 0.00999 | 0.00999 | 0.00273 | 0.00317 | 0.00317 | 0.00358 | 0.00865 | 0.00865 | 0.00206 | 0.0022 | 0.0022 | 0.22928 | 2.7747 | 156.672 | 0.07 | 3900 | 7267 | 7471 | 7681
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.025 | 4055 | 16568 | 17138 | 17727
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.03 | 3899 | 13807 | 14281 | 14772
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.035 | 3752 | 11834 | 12241 | 12662
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.04 | 3612 | 10355 | 10711 | 11079
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.045 | 3479 | 9204 | 9521 | 9848
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.05 | 3354 | 8284 | 8569 | 8863
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.055 | 3234 | 7531 | 7790 | 8058
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.06 | 3121 | 6903 | 7141 | 7386
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.065 | 3013 | 6372 | 6591 | 6818
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00382 | 0.00922 | 0.00922 | 0.00253 | 0.00294 | 0.00294 | 0.00333 | 0.00799 | 0.00799 | 0.00205 | 0.00205 | 0.00205 | 0.30767 | 3.3814 | 163.872 | 0.07 | 2911 | 5917 | 6121 | 6331
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.025 | 3388 | 14123 | 14680 | 15259
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.03 | 3241 | 11769 | 12233 | 12716
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.035 | 3103 | 10088 | 10486 | 10900
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.04 | 2973 | 8827 | 9175 | 9537
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.045 | 2851 | 7846 | 8156 | 8477
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.05 | 2736 | 7061 | 7340 | 7630
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.055 | 2627 | 6419 | 6673 | 6936
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.06 | 2525 | 5884 | 6117 | 6358
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.065 | 2428 | 5432 | 5646 | 5869
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00348 | 0.00839 | 0.00839 | 0.00231 | 0.00268 | 0.00268 | 0.00303 | 0.00726 | 0.00726 | 0.00203 | 0.00203 | 0.00203 | 0.36623 | 3.8717 | 171.072 | 0.07 | 2337 | 5044 | 5243 | 5450
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.025 | 2951 | 12450 | 12991 | 13555
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.03 | 2812 | 10375 | 10826 | 11296
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.035 | 2683 | 8893 | 9279 | 9682
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.04 | 2561 | 7781 | 8119 | 8472
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.045 | 2447 | 6917 | 7217 | 7530
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.05 | 2341 | 6225 | 6495 | 6777
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.055 | 2241 | 5659 | 5905 | 6161
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.06 | 2147 | 5188 | 5413 | 5648
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.065 | 2059 | 4789 | 4996 | 5213
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00319 | 0.00766 | 0.00766 | 0.00212 | 0.00246 | 0.00246 | 0.00278 | 0.00663 | 0.00663 | 0.00202 | 0.00202 | 0.00202 | 0.40327 | 4.2543 | 178.272 | 0.07 | 1976 | 4447 | 4640 | 4841
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.025 | 2604 | 11084 | 11607 | 12154
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.03 | 2473 | 9237 | 9672 | 10129
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.035 | 2350 | 7917 | 8291 | 8682
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.04 | 2236 | 6927 | 7254 | 7597
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.045 | 2130 | 6158 | 6448 | 6752
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.05 | 2032 | 5542 | 5803 | 6077
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.055 | 1939 | 5038 | 5276 | 5525
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.06 | 1853 | 4618 | 4836 | 5064
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.065 | 1773 | 4263 | 4464 | 4675
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.07 | 1697 | 3959 | 4145 | 4341
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.025 | 2659 | 11249 | 11750 | 12274
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.03 | 2531 | 9374 | 9792 | 10228
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.035 | 2411 | 8035 | 8393 | 8767
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.04 | 2300 | 7031 | 7344 | 7671
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.045 | 2196 | 6250 | 6528 | 6819
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.05 | 2098 | 5625 | 5875 | 6137
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.055 | 2007 | 5113 | 5341 | 5579
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.06 | 1921 | 4687 | 4896 | 5114
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.065 | 1841 | 4327 | 4519 | 4721
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00287 | 0.00684 | 0.00684 | 0.002 | 0.00221 | 0.00221 | 0.0025 | 0.00594 | 0.00594 | 0.002 | 0.002 | 0.002 | 0.43617 | 4.3636 | 192.672 | 0.07 | 1766 | 4018 | 4197 | 4384
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.025 | 2154 | 9256 | 9743 | 10256
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.035 | 1925 | 6612 | 6960 | 7326
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.04 | 1823 | 5785 | 6090 | 6410
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.045 | 1729 | 5142 | 5413 | 5698
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.05 | 1642 | 4628 | 4872 | 5128
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.055 | 1562 | 4207 | 4429 | 4662
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.06 | 1487 | 3857 | 4060 | 4273
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.065 | 1418 | 3560 | 3747 | 3945
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.07 | 1353 | 3306 | 3480 | 3663
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.025 | 1870 | 8082 | 8552 | 9049
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.03 | 1758 | 6735 | 7126 | 7541
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.035 | 1655 | 5773 | 6108 | 6463
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.04 | 1561 | 5051 | 5345 | 5656
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.045 | 1474 | 4490 | 4751 | 5027
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.05 | 1395 | 4041 | 4276 | 4524
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.055 | 1321 | 3674 | 3887 | 4113
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.06 | 1254 | 3367 | 3563 | 3770
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.065 | 1191 | 3108 | 3289 | 3480
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00248 | 0.00588 | 0.00588 | 0.00199 | 0.00199 | 0.00199 | 0.00216 | 0.00511 | 0.00511 | 0.00198 | 0.00198 | 0.00198 | 0.51142 | 5.654 | 207.072 | 0.07 | 1134 | 2886 | 3054 | 3232
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.025 | 1627 | 6776 | 7508 | 7989
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.03 | 1522 | 5665 | 6257 | 6657
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.035 | 1426 | 4870 | 5363 | 5706
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.04 | 1339 | 4271 | 4693 | 4993
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.045 | 1260 | 3805 | 4171 | 4438
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.05 | 1187 | 3430 | 3754 | 3994
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.055 | 1121 | 3124 | 3413 | 3631
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.06 | 1060 | 2866 | 3128 | 3329
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.065 | 1004 | 2649 | 2888 | 3073
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.07 | 953 | 2463 | 2682 | 2853
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.025 | 1484 | 5688 | 6871 | 7335
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.03 | 1383 | 4789 | 5726 | 6112
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.035 | 1293 | 4141 | 4908 | 5239
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.04 | 1211 | 3649 | 4295 | 4584
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.045 | 1136 | 3265 | 3817 | 4075
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.05 | 1068 | 2954 | 3436 | 3667
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.055 | 1007 | 2697 | 3123 | 3334
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.06 | 950 | 2482 | 2863 | 3056
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.065 | 899 | 2298 | 2643 | 2821
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00217 | 0.00513 | 0.00513 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00445 | 0.00445 | 0.00197 | 0.00197 | 0.00197 | 0.58796 | 6.5252 | 221.472 | 0.07 | 851 | 2141 | 2454 | 2620
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.025 | 1548 | 6552 | 7133 | 7583
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.03 | 1449 | 5471 | 5944 | 6319
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.035 | 1358 | 4697 | 5095 | 5416
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.04 | 1276 | 4116 | 4458 | 4739
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.045 | 1201 | 3663 | 3963 | 4213
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.05 | 1132 | 3300 | 3566 | 3791
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.055 | 1070 | 3003 | 3242 | 3447
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.06 | 1012 | 2754 | 2972 | 3159
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.065 | 959 | 2545 | 2743 | 2916
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.07 | 911 | 2364 | 2547 | 2708
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.025 | 1226 | 3488 | 5408 | 6143
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.03 | 1136 | 3018 | 4535 | 5119
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.035 | 1055 | 2669 | 3907 | 4388
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.04 | 983 | 2396 | 3434 | 3839
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.045 | 918 | 2177 | 3065 | 3413
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.05 | 859 | 1994 | 2767 | 3071
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.055 | 806 | 1841 | 2522 | 2792
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.06 | 758 | 1709 | 2318 | 2560
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.065 | 714 | 1594 | 2144 | 2363
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00201 | 0.00476 | 0.00476 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00414 | 0.00414 | 0.00196 | 0.00196 | 0.00196 | 0.63784 | 7.2785 | 235.872 | 0.07 | 674 | 1494 | 1994 | 2194
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.025 | 1122 | 2499 | 4522 | 5645
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.03 | 1036 | 2222 | 3832 | 4704
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.035 | 959 | 2006 | 3330 | 4032
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.04 | 891 | 1832 | 2949 | 3528
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.045 | 830 | 1686 | 2648 | 3136
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.05 | 775 | 1562 | 2403 | 2823
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.055 | 726 | 1455 | 2201 | 2566
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.06 | 681 | 1361 | 2030 | 2352
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.065 | 641 | 1277 | 1884 | 2171
36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.07 | 605 | 1203 | 1757 | 2016
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.025 | 998 | 1564 | 3308 | 4863
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.03 | 918 | 1460 | 2871 | 4076
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.035 | 846 | 1365 | 2545 | 3510
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.04 | 783 | 1279 | 2290 | 3085
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.045 | 727 | 1202 | 2084 | 2751
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.05 | 677 | 1131 | 1913 | 2484
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.055 | 632 | 1066 | 1768 | 2264
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.06 | 592 | 1007 | 1644 | 2080
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.065 | 555 | 953 | 1535 | 1924
36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00195 | 0.00422 | 0.00422 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00366 | 0.00366 | 0.00195 | 0.00195 | 0.00195 | 0.71622 | 8.2237 | 250.272 | 0.07 | 523 | 903 | 1440 | 1790
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.025 | 890 | 1402 | 2123 | 3812
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.03 | 815 | 1304 | 1935 | 3260
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.035 | 748 | 1215 | 1780 | 2855
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.04 | 690 | 1135 | 1649 | 2544
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.045 | 638 | 1062 | 1535 | 2297
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.05 | 592 | 997 | 1436 | 2095
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.055 | 552 | 937 | 1347 | 1926
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.06 | 515 | 883 | 1267 | 1782
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.065 | 483 | 833 | 1196 | 1658
36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.07 | 454 | 788 | 1131 | 1550
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.025 | 945 | 1481 | 3146 | 4613
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.03 | 869 | 1382 | 2729 | 3865
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.035 | 802 | 1293 | 2418 | 3328
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.04 | 742 | 1212 | 2175 | 2924
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.045 | 689 | 1138 | 1979 | 2608
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.05 | 641 | 1071 | 1816 | 2354
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.055 | 599 | 1010 | 1678 | 2146
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.06 | 560 | 954 | 1560 | 1971
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.065 | 526 | 903 | 1457 | 1823
36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00194 | 0.00397 | 0.00397 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77287 | 8.2095 | 264.672 | 0.07 | 495 | 856 | 1366 | 1696
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.025 | 771 | 1223 | 1588 | 2670
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.03 | 703 | 1132 | 1482 | 2366
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.035 | 642 | 1050 | 1387 | 2132
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.04 | 590 | 977 | 1300 | 1943
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.045 | 544 | 912 | 1222 | 1787
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.05 | 503 | 853 | 1150 | 1655
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.055 | 468 | 800 | 1084 | 1540
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.06 | 436 | 752 | 1024 | 1441
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.065 | 407 | 708 | 969 | 1353
36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.07 | 382 | 668 | 919 | 1275

## interior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.02 | 3059 | 15324 | 15972 | 16647
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.025 | 2915 | 12259 | 12777 | 13317
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.03 | 2781 | 10216 | 10648 | 11098
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.035 | 2656 | 8756 | 9127 | 9512
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.04 | 2538 | 7662 | 7986 | 8323
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.045 | 2428 | 6811 | 7098 | 7398
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00307 | 0.00734 | 0.00734 | 0.00203 | 0.00236 | 0.00236 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.42798 | 4.1439 | 185.472 | 0.05 | 2324 | 6130 | 6389 | 6659
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.02 | 2764 | 13942 | 14595 | 15279
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.025 | 2622 | 11154 | 11676 | 12224
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.03 | 2491 | 9295 | 9730 | 10186
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.035 | 2368 | 7967 | 8340 | 8731
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.04 | 2254 | 6971 | 7298 | 7640
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.045 | 2148 | 6196 | 6487 | 6791
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00303 | 0.00726 | 0.00726 | 0.00201 | 0.00234 | 0.00234 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.42869 | 4.5839 | 185.472 | 0.05 | 2048 | 5577 | 5838 | 6112
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.02 | 2758 | 13913 | 14566 | 15251
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.025 | 2616 | 11130 | 11653 | 12200
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.03 | 2485 | 9275 | 9711 | 10167
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.035 | 2362 | 7950 | 8324 | 8715
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.04 | 2248 | 6956 | 7283 | 7625
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.045 | 2142 | 6183 | 6474 | 6778
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.003 | 0.00719 | 0.00719 | 0.00201 | 0.00232 | 0.00232 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.42992 | 4.5904 | 185.472 | 0.05 | 2043 | 5565 | 5827 | 6100
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.02 | 2752 | 13884 | 14537 | 15222
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.025 | 2610 | 11107 | 11630 | 12177
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.035 | 2356 | 7934 | 8307 | 8698
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.04 | 2242 | 6942 | 7269 | 7611
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.045 | 2136 | 6171 | 6461 | 6765
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00297 | 0.00711 | 0.00711 | 0.00201 | 0.00229 | 0.00229 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.4312 | 4.5973 | 185.472 | 0.05 | 2037 | 5554 | 5815 | 6089
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.02 | 2746 | 13855 | 14509 | 15193
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.025 | 2604 | 11084 | 11607 | 12154
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.03 | 2473 | 9237 | 9672 | 10129
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.035 | 2350 | 7917 | 8291 | 8682
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.04 | 2236 | 6927 | 7254 | 7597
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.045 | 2130 | 6158 | 6448 | 6752
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00295 | 0.00703 | 0.00703 | 0.00201 | 0.00227 | 0.00227 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.43276 | 4.6056 | 185.472 | 0.05 | 2032 | 5542 | 5803 | 6077
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.02 | 2542 | 12830 | 13437 | 14072
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.025 | 2411 | 10264 | 10749 | 11258
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.03 | 2289 | 8553 | 8958 | 9381
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.035 | 2176 | 7331 | 7678 | 8041
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.04 | 2070 | 6415 | 6718 | 7036
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.045 | 1972 | 5702 | 5972 | 6254
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00269 | 0.00639 | 0.00639 | 0.00199 | 0.00207 | 0.00207 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.45147 | 4.6229 | 199.872 | 0.05 | 1880 | 5132 | 5375 | 5629
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.02 | 2284 | 11570 | 12179 | 12820
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.025 | 2154 | 9256 | 9743 | 10256
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.035 | 1925 | 6612 | 6960 | 7326
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.04 | 1823 | 5785 | 6090 | 6410
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.045 | 1729 | 5142 | 5413 | 5698
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00266 | 0.00633 | 0.00633 | 0.00199 | 0.00205 | 0.00205 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.45568 | 5.1333 | 199.872 | 0.05 | 1642 | 4628 | 4872 | 5128
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.02 | 2270 | 11502 | 12111 | 12752
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.025 | 2141 | 9202 | 9689 | 10202
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.035 | 1912 | 6573 | 6921 | 7287
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.04 | 1810 | 5751 | 6056 | 6376
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.045 | 1717 | 5112 | 5383 | 5668
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00263 | 0.00626 | 0.00626 | 0.00199 | 0.00203 | 0.00203 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.46099 | 5.1631 | 199.872 | 0.05 | 1630 | 4601 | 4844 | 5101
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.02 | 2252 | 11412 | 12021 | 12663
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.025 | 2123 | 9130 | 9617 | 10130
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.03 | 2004 | 7608 | 8014 | 8442
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.035 | 1894 | 6521 | 6869 | 7236
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.04 | 1793 | 5706 | 6011 | 6331
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.045 | 1700 | 5072 | 5343 | 5628
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00261 | 0.0062 | 0.0062 | 0.00199 | 0.00201 | 0.00201 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.467 | 5.1967 | 199.872 | 0.05 | 1614 | 4565 | 4808 | 5065
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.02 | 2234 | 11323 | 11932 | 12574
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.025 | 2105 | 9058 | 9546 | 10059
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.03 | 1986 | 7549 | 7955 | 8383
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.035 | 1877 | 6470 | 6818 | 7185
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.04 | 1776 | 5661 | 5966 | 6287
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.045 | 1683 | 5032 | 5303 | 5588
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00258 | 0.00613 | 0.00613 | 0.00199 | 0.00199 | 0.00199 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.47434 | 5.2373 | 199.872 | 0.05 | 1597 | 4529 | 4773 | 5030
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.02 | 1947 | 9874 | 10442 | 11042
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.025 | 1829 | 7899 | 8354 | 8834
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.03 | 1720 | 6583 | 6961 | 7362
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.035 | 1620 | 5642 | 5967 | 6310
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.04 | 1529 | 4937 | 5221 | 5521
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.045 | 1445 | 4389 | 4641 | 4908
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00238 | 0.00565 | 0.00565 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.56606 | 5.5873 | 214.272 | 0.05 | 1367 | 3950 | 4177 | 4417
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.02 | 1750 | 8506 | 9418 | 10018
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.025 | 1633 | 6830 | 7534 | 8014
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.03 | 1528 | 5709 | 6278 | 6679
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.035 | 1432 | 4906 | 5381 | 5725
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.04 | 1345 | 4302 | 4709 | 5009
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.045 | 1265 | 3831 | 4186 | 4452
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00236 | 0.0056 | 0.0056 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.56742 | 6.1828 | 214.272 | 0.05 | 1192 | 3453 | 3767 | 4007
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.02 | 1747 | 8471 | 9401 | 10002
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.025 | 1630 | 6803 | 7521 | 8001
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.03 | 1525 | 5687 | 6268 | 6668
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.035 | 1429 | 4888 | 5372 | 5715
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.04 | 1342 | 4287 | 4701 | 5001
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.045 | 1262 | 3818 | 4178 | 4445
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00234 | 0.00554 | 0.00554 | 0.00198 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.56901 | 6.1915 | 214.272 | 0.05 | 1190 | 3442 | 3761 | 4001
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.02 | 1744 | 8435 | 9385 | 9986
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.025 | 1627 | 6776 | 7508 | 7989
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.03 | 1522 | 5665 | 6257 | 6657
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.035 | 1426 | 4870 | 5363 | 5706
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.04 | 1339 | 4271 | 4693 | 4993
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.045 | 1260 | 3805 | 4171 | 4438
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00231 | 0.00548 | 0.00548 | 0.00198 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.57068 | 6.2006 | 214.272 | 0.05 | 1187 | 3430 | 3754 | 3994
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.02 | 1740 | 8399 | 9369 | 9970
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.025 | 1624 | 6748 | 7496 | 7976
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.03 | 1519 | 5644 | 6246 | 6646
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.035 | 1423 | 4852 | 5354 | 5697
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.04 | 1336 | 4256 | 4685 | 4985
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.045 | 1257 | 3792 | 4164 | 4431
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00229 | 0.00542 | 0.00542 | 0.00198 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.57272 | 6.2116 | 214.272 | 0.05 | 1184 | 3419 | 3748 | 3988
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.02 | 1657 | 8171 | 8916 | 9478
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.025 | 1548 | 6552 | 7133 | 7583
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.03 | 1449 | 5471 | 5944 | 6319
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.035 | 1358 | 4697 | 5095 | 5416
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.04 | 1276 | 4116 | 4458 | 4739
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.045 | 1201 | 3663 | 3963 | 4213
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00214 | 0.00506 | 0.00506 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58979 | 6.1227 | 228.672 | 0.05 | 1132 | 3300 | 3566 | 3791
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.02 | 1477 | 5900 | 7956 | 8516
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.025 | 1371 | 4821 | 6365 | 6813
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.03 | 1275 | 4089 | 5304 | 5677
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.035 | 1189 | 3557 | 4546 | 4866
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.04 | 1111 | 3152 | 3978 | 4258
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.045 | 1041 | 2832 | 3536 | 3785
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00211 | 0.00501 | 0.00501 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.59522 | 6.7982 | 228.672 | 0.05 | 977 | 2571 | 3182 | 3406
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.02 | 1468 | 5766 | 7904 | 8464
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.025 | 1362 | 4719 | 6323 | 6771
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.03 | 1266 | 4008 | 5270 | 5643
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.035 | 1180 | 3490 | 4517 | 4836
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.04 | 1103 | 3095 | 3952 | 4232
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.045 | 1033 | 2783 | 3513 | 3762
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00209 | 0.00496 | 0.00496 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.60202 | 6.8369 | 228.672 | 0.05 | 969 | 2529 | 3162 | 3386
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.02 | 1458 | 5633 | 7853 | 8412
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.025 | 1352 | 4617 | 6282 | 6730
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.03 | 1257 | 3926 | 5235 | 5608
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.035 | 1171 | 3423 | 4487 | 4807
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.04 | 1094 | 3039 | 3926 | 4206
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.045 | 1024 | 2734 | 3490 | 3739
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00207 | 0.00491 | 0.00491 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.60969 | 6.8803 | 228.672 | 0.05 | 961 | 2486 | 3141 | 3365
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.02 | 1444 | 5432 | 7777 | 8336
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.025 | 1339 | 4464 | 6221 | 6669
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.03 | 1244 | 3804 | 5185 | 5557
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.035 | 1158 | 3323 | 4444 | 4763
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.04 | 1081 | 2954 | 3888 | 4168
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.045 | 1012 | 2660 | 3456 | 3705
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00205 | 0.00486 | 0.00486 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.62066 | 6.942 | 228.672 | 0.05 | 949 | 2421 | 3111 | 3334
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.02 | 1376 | 5362 | 7412 | 7938
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.025 | 1277 | 4392 | 5929 | 6351
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.03 | 1187 | 3732 | 4941 | 5292
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.035 | 1106 | 3252 | 4235 | 4536
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.04 | 1033 | 2885 | 3706 | 3969
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.045 | 967 | 2595 | 3294 | 3528
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00457 | 0.00457 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.64894 | 6.8624 | 243.072 | 0.05 | 908 | 2359 | 2965 | 3175
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.02 | 1223 | 2974 | 5623 | 7088
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.025 | 1127 | 2571 | 4581 | 5670
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.03 | 1041 | 2279 | 3878 | 4725
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.035 | 964 | 2053 | 3368 | 4050
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.04 | 896 | 1872 | 2980 | 3544
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.045 | 835 | 1720 | 2674 | 3150
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00452 | 0.00452 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.65423 | 7.6156 | 243.072 | 0.05 | 780 | 1592 | 2426 | 2835
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.02 | 1218 | 2880 | 5544 | 7057
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.025 | 1122 | 2499 | 4522 | 5645
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.03 | 1036 | 2222 | 3832 | 4704
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.035 | 959 | 2006 | 3330 | 4032
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.04 | 891 | 1832 | 2949 | 3528
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.045 | 830 | 1686 | 2648 | 3136
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00447 | 0.00447 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.66074 | 7.6534 | 243.072 | 0.05 | 775 | 1562 | 2403 | 2823
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.02 | 1209 | 2723 | 5413 | 7006
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.025 | 1113 | 2380 | 4424 | 5605
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.03 | 1027 | 2126 | 3755 | 4670
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.035 | 951 | 1927 | 3268 | 4003
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.04 | 883 | 1765 | 2897 | 3503
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.045 | 822 | 1628 | 2604 | 3114
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00443 | 0.00443 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.66819 | 7.6964 | 243.072 | 0.05 | 768 | 1512 | 2365 | 2802
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.02 | 1200 | 2566 | 5282 | 6955
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.025 | 1104 | 2260 | 4326 | 5564
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.03 | 1019 | 2031 | 3678 | 4637
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.035 | 943 | 1848 | 3206 | 3974
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.04 | 875 | 1698 | 2846 | 3478
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.045 | 815 | 1571 | 2560 | 3091
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00438 | 0.00438 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.678 | 7.7527 | 243.072 | 0.05 | 761 | 1461 | 2327 | 2782
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.02 | 1136 | 2482 | 5036 | 6585
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.025 | 1046 | 2179 | 4121 | 5268
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.03 | 965 | 1953 | 3501 | 4390
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.035 | 893 | 1775 | 3051 | 3763
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.04 | 829 | 1629 | 2706 | 3293
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.045 | 772 | 1505 | 2433 | 2927
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.72703 | 7.7294 | 257.472 | 0.05 | 721 | 1398 | 2211 | 2634
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.02 | 990 | 1531 | 2614 | 4832
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.025 | 903 | 1421 | 2308 | 3967
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.03 | 827 | 1322 | 2080 | 3378
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.035 | 760 | 1233 | 1898 | 2949
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.04 | 701 | 1152 | 1747 | 2621
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.045 | 649 | 1079 | 1618 | 2361
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00411 | 0.00411 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.75604 | 8.7118 | 257.472 | 0.05 | 603 | 1013 | 1507 | 2149
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.02 | 981 | 1518 | 2441 | 4684
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.025 | 894 | 1408 | 2179 | 3859
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.03 | 818 | 1309 | 1979 | 3295
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.035 | 752 | 1220 | 1816 | 2883
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.04 | 693 | 1140 | 1678 | 2567
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.045 | 641 | 1067 | 1560 | 2316
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00407 | 0.00407 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.76836 | 8.7825 | 257.472 | 0.05 | 595 | 1001 | 1457 | 2111
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.02 | 978 | 1514 | 2391 | 4642
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.025 | 891 | 1404 | 2142 | 3828
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.03 | 816 | 1306 | 1950 | 3271
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.035 | 749 | 1217 | 1792 | 2864
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.04 | 691 | 1136 | 1659 | 2552
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.045 | 639 | 1064 | 1543 | 2303
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00403 | 0.00403 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.77077 | 8.7962 | 257.472 | 0.05 | 593 | 998 | 1443 | 2100
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.02 | 977 | 1512 | 2367 | 4621
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.025 | 890 | 1402 | 2123 | 3812
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.03 | 815 | 1304 | 1935 | 3260
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.035 | 748 | 1215 | 1780 | 2855
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.04 | 690 | 1135 | 1649 | 2544
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.045 | 638 | 1062 | 1535 | 2297
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00399 | 0.00399 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.77343 | 8.8114 | 257.472 | 0.05 | 592 | 997 | 1436 | 2095
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.02 | 962 | 1486 | 2920 | 4957
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.025 | 879 | 1381 | 2520 | 4036
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.03 | 806 | 1286 | 2231 | 3414
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.035 | 742 | 1201 | 2009 | 2963
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.04 | 685 | 1124 | 1830 | 2621
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.045 | 635 | 1053 | 1682 | 2351
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00381 | 0.00381 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.78613 | 8.5218 | 271.872 | 0.05 | 590 | 990 | 1557 | 2133
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.02 | 851 | 1324 | 1704 | 3093
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.025 | 771 | 1223 | 1588 | 2670
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.03 | 703 | 1132 | 1482 | 2366
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.035 | 642 | 1050 | 1387 | 2132
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.04 | 590 | 977 | 1300 | 1943
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.045 | 544 | 912 | 1222 | 1787
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00377 | 0.00377 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.7915 | 9.451 | 271.872 | 0.05 | 503 | 853 | 1150 | 1655
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.02 | 847 | 1318 | 1696 | 3013
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.025 | 767 | 1216 | 1580 | 2612
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.03 | 699 | 1126 | 1475 | 2321
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.035 | 639 | 1045 | 1380 | 2096
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.04 | 586 | 972 | 1293 | 1914
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.045 | 540 | 907 | 1215 | 1763
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00373 | 0.00373 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.7976 | 9.4874 | 271.872 | 0.05 | 500 | 848 | 1143 | 1634
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.02 | 842 | 1312 | 1688 | 2933
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.025 | 763 | 1210 | 1572 | 2553
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.03 | 695 | 1120 | 1467 | 2276
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.035 | 635 | 1039 | 1372 | 2060
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.04 | 583 | 966 | 1286 | 1885
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.045 | 537 | 901 | 1208 | 1739
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00369 | 0.00369 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.8054 | 9.5336 | 271.872 | 0.05 | 497 | 843 | 1136 | 1614
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.02 | 836 | 1303 | 1677 | 2813
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.025 | 757 | 1201 | 1561 | 2465
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.03 | 689 | 1111 | 1456 | 2208
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.035 | 629 | 1030 | 1362 | 2007
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.04 | 577 | 958 | 1276 | 1841
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.045 | 532 | 893 | 1197 | 1702
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00365 | 0.00365 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.81492 | 9.5898 | 271.872 | 0.05 | 492 | 835 | 1126 | 1583

## exterior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.02 | 2980 | 14959 | 15608 | 16286
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.025 | 2837 | 11967 | 12487 | 13029
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.03 | 2703 | 9972 | 10405 | 10857
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.035 | 2578 | 8548 | 8919 | 9306
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.04 | 2462 | 7479 | 7804 | 8143
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.045 | 2352 | 6648 | 6937 | 7238
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00381 | 0.00793 | 0.00303 | 0.00201 | 0.00255 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00201 | 0.00201 | 0.45036 | 4.2508 | 185.472 | 0.05 | 2250 | 5983 | 6243 | 6514
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.02 | 2692 | 13599 | 14253 | 14939
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.025 | 2551 | 10879 | 11402 | 11951
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.03 | 2420 | 9066 | 9502 | 9959
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.035 | 2298 | 7771 | 8145 | 8537
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.04 | 2185 | 6799 | 7127 | 7469
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.045 | 2080 | 6044 | 6335 | 6640
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00456 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00252 | 0.00265 | 0.0063 | 0.0063 | 0.00201 | 0.00201 | 0.00201 | 0.45 | 4.6964 | 185.472 | 0.05 | 1982 | 5439 | 5701 | 5976
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.02 | 2698 | 13627 | 14281 | 14967
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.025 | 2557 | 10901 | 11425 | 11973
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00262 | 0.00623 | 0.00623 | 0.00201 | 0.00201 | 0.00201 | 0.44973 | 4.695 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.02 | 2698 | 13627 | 14281 | 14967
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.025 | 2557 | 10901 | 11425 | 11973
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.0037 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00259 | 0.00615 | 0.00615 | 0.00201 | 0.00201 | 0.00201 | 0.44942 | 4.6934 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.02 | 2698 | 13627 | 14281 | 14967
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.025 | 2557 | 10901 | 11425 | 11973
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.03 | 2426 | 9085 | 9521 | 9978
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.035 | 2304 | 7787 | 8161 | 8552
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.04 | 2191 | 6813 | 7141 | 7483
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.045 | 2086 | 6056 | 6347 | 6652
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00442 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00245 | 0.00256 | 0.00608 | 0.00608 | 0.00201 | 0.00201 | 0.00201 | 0.44914 | 4.6919 | 185.472 | 0.05 | 1988 | 5451 | 5712 | 5987
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.02 | 2548 | 12857 | 13463 | 14099
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.025 | 2417 | 10285 | 10771 | 11279
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.03 | 2294 | 8571 | 8976 | 9399
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.035 | 2181 | 7347 | 7693 | 8056
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.04 | 2075 | 6428 | 6732 | 7049
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.045 | 1977 | 5714 | 5984 | 6266
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00234 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.44881 | 4.6093 | 199.872 | 0.05 | 1885 | 5143 | 5385 | 5639
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.02 | 2302 | 11662 | 12271 | 12912
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.025 | 2173 | 9330 | 9817 | 10330
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.035 | 1943 | 6664 | 7012 | 7378
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.04 | 1841 | 5831 | 6136 | 6456
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.045 | 1747 | 5183 | 5454 | 5739
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.44884 | 5.0946 | 199.872 | 0.05 | 1659 | 4665 | 4908 | 5165
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.02 | 2302 | 11662 | 12271 | 12912
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.025 | 2173 | 9330 | 9817 | 10330
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.035 | 1943 | 6664 | 7012 | 7378
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.04 | 1841 | 5831 | 6136 | 6456
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.045 | 1747 | 5183 | 5454 | 5739
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.0023 | 0.00544 | 0.00544 | 0.00199 | 0.00199 | 0.00199 | 0.44889 | 5.0949 | 199.872 | 0.05 | 1659 | 4665 | 4908 | 5165
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.02 | 2297 | 11639 | 12248 | 12889
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.025 | 2168 | 9311 | 9798 | 10311
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.03 | 2049 | 7759 | 8165 | 8593
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.035 | 1939 | 6651 | 6999 | 7365
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.04 | 1837 | 5820 | 6124 | 6444
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.045 | 1742 | 5173 | 5444 | 5728
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00217 | 0.00227 | 0.00538 | 0.00538 | 0.00199 | 0.00199 | 0.00199 | 0.44896 | 5.0953 | 199.872 | 0.05 | 1655 | 4656 | 4899 | 5156
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.02 | 2297 | 11639 | 12248 | 12889
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.025 | 2168 | 9311 | 9798 | 10311
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.03 | 2049 | 7759 | 8165 | 8593
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.035 | 1939 | 6651 | 6999 | 7365
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.04 | 1837 | 5820 | 6124 | 6444
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.045 | 1742 | 5173 | 5444 | 5728
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00386 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00224 | 0.00531 | 0.00531 | 0.00199 | 0.00199 | 0.00199 | 0.4491 | 5.0961 | 199.872 | 0.05 | 1655 | 4656 | 4899 | 5156
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.02 | 2192 | 11097 | 11665 | 12262
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.025 | 2071 | 8878 | 9332 | 9810
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.03 | 1959 | 7398 | 7777 | 8175
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.035 | 1855 | 6341 | 6666 | 7007
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.04 | 1760 | 5549 | 5833 | 6131
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.045 | 1671 | 4932 | 5185 | 5450
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00208 | 0.00493 | 0.00493 | 0.00198 | 0.00198 | 0.00198 | 0.45132 | 4.989 | 214.272 | 0.05 | 1588 | 4439 | 4666 | 4905
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.02 | 1973 | 10007 | 10574 | 11175
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.025 | 1854 | 8005 | 8460 | 8940
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.035 | 1645 | 5718 | 6043 | 6385
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.04 | 1553 | 5003 | 5287 | 5587
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.045 | 1468 | 4447 | 4700 | 4966
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00206 | 0.00487 | 0.00487 | 0.00198 | 0.00198 | 0.00198 | 0.45187 | 5.5175 | 214.272 | 0.05 | 1390 | 4003 | 4230 | 4470
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.02 | 1973 | 10007 | 10574 | 11175
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.025 | 1854 | 8005 | 8460 | 8940
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.035 | 1645 | 5718 | 6043 | 6385
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.04 | 1553 | 5003 | 5287 | 5587
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.045 | 1468 | 4447 | 4700 | 4966
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00203 | 0.00482 | 0.00482 | 0.00198 | 0.00198 | 0.00198 | 0.45266 | 5.5223 | 214.272 | 0.05 | 1390 | 4003 | 4230 | 4470
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.02 | 1970 | 9988 | 10555 | 11156
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.025 | 1851 | 7990 | 8444 | 8924
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.035 | 1641 | 5707 | 6032 | 6375
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.04 | 1550 | 4994 | 5278 | 5578
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.045 | 1465 | 4439 | 4691 | 4958
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00201 | 0.00476 | 0.00476 | 0.00198 | 0.00198 | 0.00198 | 0.45353 | 5.5276 | 214.272 | 0.05 | 1387 | 3995 | 4222 | 4462
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.02 | 1970 | 9988 | 10555 | 11156
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.025 | 1851 | 7990 | 8444 | 8924
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.035 | 1641 | 5707 | 6032 | 6375
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.04 | 1550 | 4994 | 5278 | 5578
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.045 | 1465 | 4439 | 4691 | 4958
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00585 | 0.00227 | 0.00198 | 0.00198 | 0.00199 | 0.00471 | 0.00471 | 0.00198 | 0.00198 | 0.00198 | 0.45449 | 5.5335 | 214.272 | 0.05 | 1387 | 3995 | 4222 | 4462
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.02 | 1885 | 9558 | 10090 | 10652
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.025 | 1773 | 7646 | 8072 | 8522
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.03 | 1670 | 6372 | 6727 | 7101
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.035 | 1576 | 5462 | 5766 | 6087
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.04 | 1489 | 4779 | 5045 | 5326
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.045 | 1409 | 4248 | 4484 | 4734
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.46264 | 5.4227 | 228.672 | 0.05 | 1335 | 3823 | 4036 | 4261
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.02 | 1689 | 8539 | 9086 | 9649
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.025 | 1580 | 6833 | 7269 | 7719
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.03 | 1480 | 5695 | 6058 | 6433
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.035 | 1389 | 4881 | 5192 | 5514
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.04 | 1306 | 4272 | 4543 | 4825
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.045 | 1230 | 3798 | 4038 | 4289
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00436 | 0.00436 | 0.00196 | 0.00196 | 0.00196 | 0.46497 | 6.0085 | 228.672 | 0.05 | 1161 | 3418 | 3635 | 3860
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.02 | 1683 | 8472 | 9055 | 9618
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.025 | 1574 | 6782 | 7244 | 7694
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.03 | 1474 | 5654 | 6037 | 6412
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.035 | 1384 | 4848 | 5174 | 5496
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.04 | 1301 | 4243 | 4528 | 4809
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.045 | 1225 | 3773 | 4024 | 4275
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00207 | 0.00196 | 0.00196 | 0.00196 | 0.00431 | 0.00431 | 0.00196 | 0.00196 | 0.00196 | 0.46768 | 6.026 | 228.672 | 0.05 | 1156 | 3397 | 3622 | 3847
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.02 | 1677 | 8405 | 9024 | 9587
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.025 | 1568 | 6731 | 7219 | 7669
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.03 | 1469 | 5613 | 6016 | 6391
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.035 | 1378 | 4814 | 5156 | 5478
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.04 | 1295 | 4215 | 4512 | 4793
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.045 | 1220 | 3749 | 4011 | 4261
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00309 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00426 | 0.00426 | 0.00196 | 0.00196 | 0.00196 | 0.47064 | 6.0451 | 228.672 | 0.05 | 1151 | 3375 | 3610 | 3835
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.02 | 1671 | 8338 | 8993 | 9556
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.025 | 1562 | 6680 | 7194 | 7644
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.03 | 1463 | 5573 | 5995 | 6370
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.035 | 1372 | 4781 | 5139 | 5460
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.04 | 1290 | 4187 | 4496 | 4778
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.045 | 1214 | 3724 | 3997 | 4247
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00306 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00421 | 0.00421 | 0.00196 | 0.00196 | 0.00196 | 0.47418 | 6.0678 | 228.672 | 0.05 | 1145 | 3354 | 3597 | 3822
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.02 | 1595 | 8079 | 8578 | 9107
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.025 | 1492 | 6463 | 6862 | 7286
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.03 | 1398 | 5386 | 5719 | 6072
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.035 | 1312 | 4617 | 4902 | 5204
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.04 | 1234 | 4040 | 4289 | 4554
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.045 | 1163 | 3591 | 3812 | 4048
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.49462 | 5.9912 | 243.072 | 0.05 | 1097 | 3232 | 3431 | 3643
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.02 | 1419 | 5959 | 7646 | 8174
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.025 | 1319 | 4847 | 6117 | 6539
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.03 | 1228 | 4095 | 5098 | 5449
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.035 | 1147 | 3551 | 4369 | 4671
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.04 | 1073 | 3139 | 3823 | 4087
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.045 | 1006 | 2813 | 3398 | 3633
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00238 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00393 | 0.00393 | 0.00195 | 0.00195 | 0.00195 | 0.50207 | 6.6715 | 243.072 | 0.05 | 945 | 2550 | 3059 | 3269
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.02 | 1406 | 5770 | 7571 | 8098
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.025 | 1305 | 4703 | 6057 | 6479
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.03 | 1215 | 3981 | 5047 | 5399
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.035 | 1134 | 3457 | 4326 | 4628
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.04 | 1060 | 3059 | 3786 | 4049
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.045 | 993 | 2744 | 3365 | 3599
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00389 | 0.00389 | 0.00195 | 0.00195 | 0.00195 | 0.5116 | 6.7345 | 243.072 | 0.05 | 933 | 2490 | 3028 | 3239
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.02 | 1387 | 5519 | 7473 | 7999
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.025 | 1287 | 4512 | 5978 | 6399
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.03 | 1198 | 3828 | 4982 | 5333
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.035 | 1117 | 3331 | 4270 | 4571
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.04 | 1043 | 2952 | 3736 | 4000
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.045 | 977 | 2652 | 3321 | 3555
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00384 | 0.00384 | 0.00195 | 0.00195 | 0.00195 | 0.52323 | 6.8106 | 243.072 | 0.05 | 917 | 2409 | 2989 | 3200
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.02 | 1365 | 5205 | 7352 | 7878
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.025 | 1266 | 4272 | 5881 | 6302
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.03 | 1176 | 3637 | 4901 | 5252
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.035 | 1096 | 3173 | 4201 | 4502
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.04 | 1023 | 2819 | 3676 | 3939
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.045 | 958 | 2537 | 3267 | 3501
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00277 | 0.00231 | 0.00474 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0038 | 0.0038 | 0.00195 | 0.00195 | 0.00195 | 0.53859 | 6.9098 | 243.072 | 0.05 | 898 | 2308 | 2941 | 3151
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.02 | 1277 | 4736 | 6874 | 7370
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.025 | 1183 | 3897 | 5499 | 5896
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.03 | 1099 | 3325 | 4582 | 4913
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.035 | 1023 | 2907 | 3928 | 4211
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.04 | 955 | 2586 | 3437 | 3685
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.045 | 893 | 2331 | 3055 | 3275
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00449 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.59044 | 6.9656 | 257.472 | 0.05 | 838 | 2122 | 2749 | 2948
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.02 | 1110 | 2007 | 4640 | 6435
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.025 | 1020 | 1817 | 3826 | 5148
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.03 | 940 | 1665 | 3270 | 4290
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.035 | 869 | 1537 | 2862 | 3677
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.04 | 806 | 1427 | 2549 | 3218
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.045 | 750 | 1331 | 2300 | 2860
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.61969 | 7.8872 | 257.472 | 0.05 | 699 | 1246 | 2097 | 2574
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.02 | 1097 | 1770 | 4443 | 6362
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.025 | 1008 | 1636 | 3678 | 5090
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.03 | 928 | 1520 | 3154 | 4241
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.035 | 858 | 1418 | 2768 | 3635
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.04 | 795 | 1327 | 2471 | 3181
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.045 | 739 | 1245 | 2233 | 2828
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00215 | 0.00439 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.63247 | 7.9681 | 257.472 | 0.05 | 689 | 1170 | 2039 | 2545
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.02 | 1094 | 1711 | 4393 | 6344
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.025 | 1005 | 1591 | 3640 | 5075
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.03 | 925 | 1484 | 3124 | 4229
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.035 | 855 | 1388 | 2745 | 3625
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.04 | 792 | 1302 | 2451 | 3172
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.045 | 736 | 1223 | 2217 | 2820
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.63522 | 7.9854 | 257.472 | 0.05 | 686 | 1151 | 2025 | 2538
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.02 | 1091 | 1678 | 4344 | 6314
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.025 | 1001 | 1566 | 3604 | 5052
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.03 | 922 | 1464 | 3096 | 4211
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.035 | 852 | 1371 | 2721 | 3611
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.04 | 789 | 1286 | 2432 | 3159
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.045 | 734 | 1210 | 2200 | 2809
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00346 | 0.00346 | 0.00194 | 0.00194 | 0.00194 | 0.63843 | 8.0056 | 257.472 | 0.05 | 684 | 1139 | 2010 | 2529
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.02 | 1070 | 2238 | 4675 | 6201
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.025 | 984 | 1978 | 3833 | 4960
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.03 | 908 | 1781 | 3261 | 4134
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.035 | 840 | 1624 | 2844 | 3543
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.04 | 780 | 1494 | 2525 | 3100
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.045 | 726 | 1384 | 2273 | 2756
| 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00194 | 0.00194 | 0.00194 | 0.65388 | 7.772 | 271.872 | 0.05 | 677 | 1288 | 2067 | 2480
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.02 | 948 | 1465 | 2662 | 4736
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.025 | 865 | 1361 | 2327 | 3874
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.03 | 793 | 1266 | 2080 | 3290
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.035 | 729 | 1181 | 1886 | 2865
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.04 | 673 | 1105 | 1728 | 2541
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.045 | 623 | 1035 | 1595 | 2284
| 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00199 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00328 | 0.00328 | 0.00194 | 0.00194 | 0.00194 | 0.66009 | 8.6309 | 271.872 | 0.05 | 579 | 972 | 1482 | 2076
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.02 | 941 | 1456 | 2545 | 4636
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.025 | 859 | 1351 | 2239 | 3801
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.03 | 787 | 1257 | 2012 | 3234
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.035 | 723 | 1173 | 1830 | 2820
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.04 | 667 | 1096 | 1682 | 2504
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.045 | 618 | 1027 | 1556 | 2254
| 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00194 | 0.00194 | 0.00194 | 0.66805 | 8.6828 | 271.872 | 0.05 | 574 | 964 | 1448 | 2050
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.02 | 932 | 1443 | 2381 | 4496
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.025 | 850 | 1339 | 2117 | 3698
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.03 | 778 | 1245 | 1915 | 3155
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.035 | 715 | 1161 | 1752 | 2758
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.04 | 660 | 1084 | 1617 | 2453
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.045 | 610 | 1015 | 1501 | 2212
| 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00321 | 0.00321 | 0.00194 | 0.00194 | 0.00194 | 0.6777 | 8.7452 | 271.872 | 0.05 | 567 | 953 | 1400 | 2014
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.02 | 922 | 1429 | 2194 | 4336
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.025 | 841 | 1325 | 1977 | 3581
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.03 | 769 | 1231 | 1805 | 3065
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.035 | 706 | 1147 | 1663 | 2686
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.04 | 651 | 1071 | 1543 | 2395
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.045 | 602 | 1003 | 1438 | 2163
| 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00317 | 0.00317 | 0.00194 | 0.00194 | 0.00194 | 0.69015 | 8.8252 | 271.872 | 0.05 | 559 | 941 | 1346 | 1973

## 50%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.025 | 2678 | 11367 | 11889 | 12435
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.03 | 2546 | 9472 | 9907 | 10362
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.035 | 2423 | 8119 | 8492 | 8882
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.04 | 2308 | 7104 | 7430 | 7772
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.045 | 2201 | 6315 | 6605 | 6908
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.05 | 2100 | 5683 | 5944 | 6217
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.055 | 2007 | 5167 | 5404 | 5652
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.06 | 1920 | 4736 | 4954 | 5181
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.065 | 1838 | 4372 | 4573 | 4783
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00455 | 0.00302 | 0.00383 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.00302 | 0.00302 | 0.50183 | 4.4872 | 185.472 | 0.07 | 1761 | 4060 | 4246 | 4441
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.025 | 2408 | 10318 | 10843 | 11394
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.03 | 2278 | 8598 | 9036 | 9495
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.035 | 2159 | 7370 | 7745 | 8139
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.04 | 2048 | 6449 | 6777 | 7121
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.045 | 1945 | 5732 | 6024 | 6330
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.05 | 1849 | 5159 | 5421 | 5697
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.055 | 1761 | 4690 | 4929 | 5179
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.06 | 1678 | 4299 | 4518 | 4748
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.065 | 1602 | 3969 | 4170 | 4382
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.00378 | 0.00398 | 0.00945 | 0.00945 | 0.00302 | 0.00302 | 0.00302 | 0.5028 | 4.9643 | 185.472 | 0.07 | 1530 | 3685 | 3872 | 4069
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.025 | 2403 | 10297 | 10822 | 11374
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.03 | 2273 | 8581 | 9019 | 9478
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.035 | 2154 | 7355 | 7730 | 8124
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.04 | 2043 | 6436 | 6764 | 7109
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.045 | 1940 | 5721 | 6012 | 6319
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.05 | 1845 | 5149 | 5411 | 5687
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.055 | 1756 | 4681 | 4919 | 5170
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.06 | 1674 | 4291 | 4509 | 4739
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.065 | 1597 | 3961 | 4162 | 4374
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00393 | 0.00935 | 0.00935 | 0.00302 | 0.00302 | 0.00302 | 0.5042 | 4.9712 | 185.472 | 0.07 | 1526 | 3678 | 3865 | 4062
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.025 | 2397 | 10277 | 10802 | 11353
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.03 | 2268 | 8564 | 9001 | 9461
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.035 | 2148 | 7341 | 7715 | 8109
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.04 | 2038 | 6423 | 6751 | 7096
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.045 | 1935 | 5709 | 6001 | 6307
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.05 | 1840 | 5138 | 5401 | 5677
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.055 | 1751 | 4671 | 4910 | 5161
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.06 | 1669 | 4282 | 4501 | 4730
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.065 | 1593 | 3953 | 4154 | 4367
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00388 | 0.00923 | 0.00923 | 0.00302 | 0.00302 | 0.00302 | 0.50562 | 4.9782 | 185.472 | 0.07 | 1522 | 3670 | 3858 | 4055
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.025 | 2392 | 10256 | 10781 | 11333
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.03 | 2263 | 8547 | 8984 | 9444
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.035 | 2143 | 7326 | 7701 | 8095
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.04 | 2033 | 6410 | 6738 | 7083
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.045 | 1930 | 5698 | 5989 | 6296
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.05 | 1835 | 5128 | 5391 | 5666
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.055 | 1747 | 4662 | 4900 | 5151
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.06 | 1665 | 4273 | 4492 | 4722
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.065 | 1588 | 3945 | 4147 | 4359
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00368 | 0.00384 | 0.00912 | 0.00912 | 0.00302 | 0.00302 | 0.00302 | 0.50733 | 4.9866 | 185.472 | 0.07 | 1517 | 3663 | 3850 | 4047
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.025 | 2220 | 9517 | 10004 | 10516
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.03 | 2100 | 7931 | 8337 | 8764
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.035 | 1989 | 6798 | 7146 | 7512
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.04 | 1886 | 5948 | 6253 | 6573
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.045 | 1791 | 5287 | 5558 | 5842
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.05 | 1703 | 4759 | 5002 | 5258
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.055 | 1621 | 4326 | 4547 | 4780
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.06 | 1545 | 3966 | 4169 | 4382
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.065 | 1474 | 3661 | 3848 | 4045
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00351 | 0.00836 | 0.00836 | 0.00298 | 0.00298 | 0.00298 | 0.52687 | 4.994 | 199.872 | 0.07 | 1408 | 3399 | 3573 | 3756
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.025 | 1980 | 8549 | 9036 | 9551
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.03 | 1863 | 7124 | 7530 | 7959
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.035 | 1756 | 6107 | 6455 | 6822
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.04 | 1657 | 5343 | 5648 | 5969
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.045 | 1567 | 4750 | 5020 | 5306
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.05 | 1483 | 4275 | 4518 | 4776
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.055 | 1407 | 3886 | 4107 | 4341
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.06 | 1336 | 3562 | 3765 | 3980
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.065 | 1270 | 3288 | 3476 | 3673
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00348 | 0.00826 | 0.00826 | 0.00298 | 0.00298 | 0.00298 | 0.53113 | 5.542 | 199.872 | 0.07 | 1209 | 3053 | 3227 | 3411
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.025 | 1968 | 8501 | 8988 | 9502
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.03 | 1851 | 7084 | 7490 | 7919
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.035 | 1744 | 6072 | 6420 | 6787
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.04 | 1646 | 5313 | 5617 | 5939
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.045 | 1556 | 4723 | 4993 | 5279
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.05 | 1473 | 4250 | 4494 | 4751
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.055 | 1396 | 3864 | 4085 | 4319
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.06 | 1325 | 3542 | 3745 | 3959
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.065 | 1260 | 3270 | 3457 | 3655
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00345 | 0.00816 | 0.00816 | 0.00298 | 0.00298 | 0.00298 | 0.53665 | 5.5707 | 199.872 | 0.07 | 1200 | 3036 | 3210 | 3394
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.025 | 1956 | 8453 | 8939 | 9454
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.03 | 1840 | 7044 | 7449 | 7879
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.035 | 1733 | 6038 | 6385 | 6753
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.04 | 1635 | 5283 | 5587 | 5909
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.045 | 1545 | 4696 | 4966 | 5252
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.05 | 1462 | 4226 | 4470 | 4727
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.055 | 1386 | 3842 | 4063 | 4297
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.06 | 1315 | 3522 | 3725 | 3939
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.065 | 1250 | 3251 | 3438 | 3636
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00325 | 0.00341 | 0.00807 | 0.00807 | 0.00298 | 0.00298 | 0.00298 | 0.54223 | 5.5996 | 199.872 | 0.07 | 1190 | 3019 | 3193 | 3377
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.025 | 1945 | 8405 | 8891 | 9406
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.03 | 1828 | 7004 | 7410 | 7839
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.035 | 1722 | 6003 | 6351 | 6719
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.04 | 1624 | 5253 | 5557 | 5879
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.045 | 1534 | 4669 | 4940 | 5226
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.05 | 1452 | 4202 | 4446 | 4703
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.055 | 1376 | 3820 | 4042 | 4276
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.06 | 1305 | 3502 | 3705 | 3919
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.065 | 1241 | 3233 | 3420 | 3618
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00336 | 0.00796 | 0.00796 | 0.00298 | 0.00298 | 0.00298 | 0.54886 | 5.6337 | 199.872 | 0.07 | 1181 | 3002 | 3176 | 3359
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.025 | 1745 | 7552 | 8005 | 8486
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.03 | 1637 | 6293 | 6671 | 7071
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.035 | 1539 | 5394 | 5718 | 6061
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.04 | 1449 | 4720 | 5003 | 5304
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.045 | 1367 | 4195 | 4447 | 4714
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.05 | 1292 | 3776 | 4003 | 4243
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.055 | 1222 | 3433 | 3639 | 3857
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.06 | 1159 | 3147 | 3335 | 3536
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.065 | 1100 | 2905 | 3079 | 3264
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00312 | 0.0074 | 0.0074 | 0.00297 | 0.00297 | 0.00297 | 0.61529 | 5.8252 | 214.272 | 0.07 | 1046 | 2697 | 2859 | 3031
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.025 | 1555 | 6096 | 7198 | 7677
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.03 | 1451 | 5123 | 5998 | 6398
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.035 | 1357 | 4423 | 5141 | 5484
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.04 | 1272 | 3893 | 4499 | 4798
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.045 | 1194 | 3479 | 3999 | 4265
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.05 | 1124 | 3144 | 3599 | 3839
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.055 | 1059 | 2870 | 3272 | 3490
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.06 | 1000 | 2638 | 2999 | 3199
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.065 | 946 | 2442 | 2768 | 2953
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00309 | 0.00731 | 0.00731 | 0.00297 | 0.00297 | 0.00297 | 0.61688 | 6.4467 | 214.272 | 0.07 | 897 | 2273 | 2571 | 2742
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.025 | 1553 | 6069 | 7186 | 7665
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.03 | 1449 | 5101 | 5988 | 6388
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.035 | 1355 | 4405 | 5133 | 5475
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.04 | 1269 | 3878 | 4491 | 4791
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.045 | 1192 | 3466 | 3992 | 4258
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.05 | 1121 | 3133 | 3593 | 3833
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.055 | 1057 | 2859 | 3266 | 3484
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.06 | 998 | 2629 | 2994 | 3194
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.065 | 944 | 2434 | 2764 | 2948
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00305 | 0.00723 | 0.00723 | 0.00297 | 0.00297 | 0.00297 | 0.61878 | 6.4566 | 214.272 | 0.07 | 895 | 2266 | 2566 | 2738
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.025 | 1550 | 6042 | 7174 | 7653
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.03 | 1446 | 5080 | 5978 | 6378
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.035 | 1352 | 4387 | 5124 | 5466
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.04 | 1267 | 3863 | 4483 | 4783
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.045 | 1189 | 3453 | 3985 | 4252
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.05 | 1119 | 3121 | 3587 | 3827
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.055 | 1054 | 2849 | 3261 | 3479
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.06 | 996 | 2620 | 2989 | 3189
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.065 | 942 | 2426 | 2759 | 2943
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00302 | 0.00714 | 0.00714 | 0.00297 | 0.00297 | 0.00297 | 0.62072 | 6.4667 | 214.272 | 0.07 | 893 | 2258 | 2562 | 2733
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.025 | 1547 | 6015 | 7162 | 7641
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.03 | 1443 | 5058 | 5968 | 6367
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.035 | 1349 | 4369 | 5115 | 5458
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.04 | 1264 | 3848 | 4476 | 4776
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.045 | 1187 | 3440 | 3979 | 4245
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.05 | 1116 | 3110 | 3581 | 3820
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.055 | 1052 | 2839 | 3255 | 3473
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.06 | 993 | 2611 | 2984 | 3184
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.065 | 940 | 2418 | 2754 | 2939
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00341 | 0.00297 | 0.00297 | 0.00298 | 0.00706 | 0.00706 | 0.00297 | 0.00297 | 0.00297 | 0.62327 | 6.48 | 214.272 | 0.07 | 890 | 2251 | 2558 | 2729
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.025 | 1473 | 5865 | 6813 | 7262
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.03 | 1376 | 4922 | 5677 | 6052
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.035 | 1287 | 4244 | 4866 | 5187
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.04 | 1206 | 3733 | 4258 | 4539
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.045 | 1133 | 3333 | 3785 | 4035
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.05 | 1067 | 3011 | 3406 | 3631
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.055 | 1006 | 2746 | 3097 | 3301
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.06 | 950 | 2524 | 2839 | 3026
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.065 | 899 | 2335 | 2620 | 2793
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00662 | 0.00662 | 0.00294 | 0.00294 | 0.00294 | 0.64238 | 6.3898 | 228.672 | 0.07 | 853 | 2172 | 2433 | 2594
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.025 | 1305 | 4082 | 5974 | 6519
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.03 | 1211 | 3500 | 4987 | 5432
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.035 | 1127 | 3071 | 4282 | 4656
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.04 | 1051 | 2741 | 3752 | 4074
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.045 | 982 | 2477 | 3339 | 3622
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.05 | 920 | 2261 | 3008 | 3259
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.055 | 864 | 2079 | 2737 | 2963
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.06 | 814 | 1925 | 2510 | 2716
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.065 | 767 | 1792 | 2319 | 2507
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00654 | 0.00654 | 0.00294 | 0.00294 | 0.00294 | 0.64809 | 7.0937 | 228.672 | 0.07 | 725 | 1676 | 2154 | 2328
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.025 | 1297 | 3980 | 5890 | 6480
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.03 | 1203 | 3418 | 4922 | 5400
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.035 | 1119 | 3004 | 4229 | 4628
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.04 | 1043 | 2684 | 3708 | 4050
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.045 | 975 | 2428 | 3301 | 3600
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.05 | 913 | 2218 | 2976 | 3240
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.055 | 857 | 2041 | 2709 | 2945
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.06 | 807 | 1891 | 2485 | 2700
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.065 | 761 | 1761 | 2297 | 2492
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.0031 | 0.00294 | 0.00294 | 0.00294 | 0.00646 | 0.00646 | 0.00294 | 0.00294 | 0.00294 | 0.65493 | 7.131 | 228.672 | 0.07 | 719 | 1647 | 2134 | 2314
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.025 | 1288 | 3879 | 5807 | 6441
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.03 | 1195 | 3337 | 4856 | 5368
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.035 | 1111 | 2937 | 4176 | 4601
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.04 | 1035 | 2628 | 3664 | 4026
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.045 | 967 | 2379 | 3264 | 3578
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.05 | 906 | 2175 | 2943 | 3221
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.055 | 850 | 2003 | 2680 | 2928
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.06 | 800 | 1857 | 2460 | 2684
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.065 | 754 | 1730 | 2274 | 2477
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00639 | 0.00639 | 0.00294 | 0.00294 | 0.00294 | 0.66226 | 7.1709 | 228.672 | 0.07 | 713 | 1619 | 2113 | 2300
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.025 | 1278 | 3751 | 5703 | 6393
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.03 | 1184 | 3235 | 4775 | 5328
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.035 | 1101 | 2853 | 4110 | 4567
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.04 | 1025 | 2557 | 3609 | 3996
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.045 | 958 | 2318 | 3217 | 3552
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.05 | 897 | 2121 | 2903 | 3197
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.055 | 841 | 1956 | 2645 | 2906
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.06 | 791 | 1814 | 2429 | 2664
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.065 | 746 | 1691 | 2246 | 2459
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00632 | 0.00632 | 0.00294 | 0.00294 | 0.00294 | 0.67209 | 7.2239 | 228.672 | 0.07 | 705 | 1583 | 2087 | 2283
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.025 | 1222 | 3769 | 5561 | 6105
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.03 | 1134 | 3235 | 4646 | 5088
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.035 | 1054 | 2842 | 3991 | 4361
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.04 | 983 | 2538 | 3499 | 3816
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.045 | 919 | 2295 | 3114 | 3392
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.05 | 861 | 2096 | 2807 | 3053
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.055 | 808 | 1929 | 2555 | 2775
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.06 | 760 | 1787 | 2344 | 2544
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.065 | 717 | 1664 | 2165 | 2348
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00293 | 0.00293 | 0.00293 | 0.69848 | 7.1195 | 243.072 | 0.07 | 678 | 1556 | 2012 | 2180
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.025 | 1079 | 1901 | 4032 | 5445
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.03 | 994 | 1744 | 3448 | 4538
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.035 | 919 | 1612 | 3019 | 3890
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.04 | 852 | 1498 | 2690 | 3403
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.045 | 793 | 1398 | 2428 | 3025
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.05 | 739 | 1310 | 2213 | 2723
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.055 | 691 | 1231 | 2034 | 2475
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.06 | 648 | 1159 | 1882 | 2269
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.065 | 609 | 1095 | 1751 | 2094
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0059 | 0.0059 | 0.00293 | 0.00293 | 0.00293 | 0.70402 | 7.9001 | 243.072 | 0.07 | 574 | 1036 | 1637 | 1945
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.025 | 1072 | 1805 | 3954 | 5414
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.03 | 988 | 1668 | 3386 | 4512
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.035 | 913 | 1549 | 2969 | 3867
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.04 | 846 | 1445 | 2649 | 3384
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.045 | 787 | 1352 | 2392 | 3008
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.05 | 734 | 1270 | 2183 | 2707
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.055 | 686 | 1195 | 2008 | 2461
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.06 | 643 | 1127 | 1858 | 2256
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.065 | 604 | 1066 | 1729 | 2082
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00583 | 0.00583 | 0.00293 | 0.00293 | 0.00293 | 0.71071 | 7.9375 | 243.072 | 0.07 | 569 | 1009 | 1617 | 1934
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.025 | 1066 | 1709 | 3876 | 5383
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.03 | 982 | 1591 | 3325 | 4486
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.035 | 907 | 1486 | 2919 | 3845
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.04 | 840 | 1392 | 2607 | 3365
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.045 | 781 | 1306 | 2357 | 2991
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.05 | 728 | 1229 | 2152 | 2692
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.055 | 681 | 1159 | 1981 | 2447
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.06 | 638 | 1095 | 1834 | 2243
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.065 | 600 | 1037 | 1708 | 2071
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00576 | 0.00576 | 0.00293 | 0.00293 | 0.00293 | 0.71818 | 7.9791 | 243.072 | 0.07 | 565 | 982 | 1598 | 1923
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.025 | 1058 | 1654 | 3778 | 5319
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.03 | 974 | 1546 | 3248 | 4435
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.035 | 899 | 1447 | 2857 | 3804
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.04 | 833 | 1358 | 2555 | 3331
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.045 | 774 | 1277 | 2313 | 2962
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.05 | 722 | 1203 | 2114 | 2667
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.055 | 674 | 1135 | 1947 | 2425
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.06 | 632 | 1073 | 1805 | 2224
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.065 | 594 | 1016 | 1682 | 2054
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.0057 | 0.0057 | 0.00293 | 0.00293 | 0.00293 | 0.72774 | 8.032 | 243.072 | 0.07 | 559 | 964 | 1574 | 1907
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.025 | 1009 | 1658 | 3696 | 5097
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.03 | 930 | 1538 | 3168 | 4247
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.035 | 859 | 1433 | 2780 | 3641
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.04 | 796 | 1339 | 2481 | 3186
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.045 | 740 | 1255 | 2242 | 2832
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.05 | 690 | 1179 | 2046 | 2548
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.055 | 645 | 1111 | 1882 | 2317
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.06 | 605 | 1048 | 1743 | 2124
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.065 | 568 | 993 | 1623 | 1960
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.77072 | 7.9582 | 257.472 | 0.07 | 535 | 940 | 1518 | 1820
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.025 | 876 | 1382 | 1920 | 3642
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.03 | 801 | 1284 | 1776 | 3129
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.035 | 735 | 1196 | 1651 | 2751
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.04 | 677 | 1116 | 1541 | 2460
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.045 | 626 | 1044 | 1444 | 2226
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.05 | 581 | 979 | 1356 | 2035
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.055 | 541 | 920 | 1277 | 1874
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.06 | 505 | 866 | 1206 | 1738
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.065 | 473 | 818 | 1141 | 1619
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.79273 | 8.9207 | 257.472 | 0.07 | 444 | 773 | 1081 | 1515
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.025 | 870 | 1373 | 1827 | 3564
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.03 | 795 | 1275 | 1703 | 3069
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.035 | 730 | 1187 | 1592 | 2704
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.04 | 672 | 1108 | 1492 | 2421
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.045 | 621 | 1036 | 1402 | 2194
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.05 | 576 | 971 | 1321 | 2008
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.055 | 536 | 912 | 1246 | 1851
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.06 | 501 | 859 | 1178 | 1717
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.065 | 469 | 811 | 1116 | 1601
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.80171 | 8.9711 | 257.472 | 0.07 | 440 | 766 | 1059 | 1499
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.025 | 869 | 1371 | 1809 | 3549
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.03 | 794 | 1273 | 1689 | 3057
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.035 | 729 | 1185 | 1581 | 2694
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.04 | 671 | 1106 | 1483 | 2413
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.045 | 620 | 1034 | 1394 | 2188
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.05 | 575 | 970 | 1313 | 2002
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.055 | 535 | 911 | 1240 | 1846
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.06 | 500 | 858 | 1172 | 1713
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.065 | 468 | 809 | 1111 | 1597
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.80403 | 8.984 | 257.472 | 0.07 | 439 | 765 | 1054 | 1496
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.025 | 867 | 1368 | 1772 | 3518
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.03 | 792 | 1270 | 1660 | 3034
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.035 | 726 | 1182 | 1557 | 2676
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.04 | 669 | 1103 | 1463 | 2398
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.045 | 618 | 1031 | 1377 | 2175
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.05 | 573 | 967 | 1299 | 1992
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.055 | 533 | 908 | 1227 | 1837
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.06 | 498 | 855 | 1161 | 1705
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.065 | 466 | 807 | 1101 | 1590
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00519 | 0.00519 | 0.00291 | 0.00291 | 0.00291 | 0.80675 | 8.9992 | 257.472 | 0.07 | 438 | 762 | 1045 | 1490
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.025 | 856 | 1348 | 2204 | 3771
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.03 | 784 | 1254 | 1984 | 3211
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.035 | 721 | 1169 | 1808 | 2802
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.04 | 665 | 1093 | 1663 | 2490
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.045 | 616 | 1024 | 1540 | 2242
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.05 | 572 | 961 | 1434 | 2040
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.055 | 533 | 904 | 1341 | 1872
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.06 | 498 | 852 | 1259 | 1730
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.065 | 467 | 805 | 1186 | 1608
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.00291 | 0.00291 | 0.00291 | 0.81874 | 8.6968 | 271.872 | 0.07 | 438 | 761 | 1119 | 1502
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.025 | 752 | 1194 | 1552 | 2391
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.03 | 684 | 1104 | 1447 | 2152
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.035 | 625 | 1023 | 1353 | 1962
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.04 | 573 | 951 | 1267 | 1804
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.045 | 528 | 887 | 1189 | 1672
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.05 | 488 | 829 | 1118 | 1557
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.055 | 453 | 776 | 1054 | 1456
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.06 | 422 | 729 | 995 | 1368
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.065 | 394 | 686 | 941 | 1288
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00492 | 0.00492 | 0.00291 | 0.00291 | 0.00291 | 0.82355 | 9.6405 | 271.872 | 0.07 | 370 | 648 | 891 | 1217
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.025 | 749 | 1189 | 1546 | 2347
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.03 | 681 | 1099 | 1442 | 2118
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.035 | 622 | 1019 | 1347 | 1935
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.04 | 570 | 947 | 1262 | 1783
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.045 | 525 | 883 | 1184 | 1654
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.05 | 486 | 825 | 1113 | 1542
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.055 | 451 | 773 | 1049 | 1443
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.06 | 420 | 726 | 990 | 1356
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.065 | 392 | 683 | 936 | 1278
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.00291 | 0.00291 | 0.00291 | 0.82904 | 9.6726 | 271.872 | 0.07 | 368 | 644 | 887 | 1208
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.025 | 745 | 1183 | 1539 | 2289
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.03 | 677 | 1094 | 1435 | 2073
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.035 | 618 | 1013 | 1340 | 1899
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.04 | 567 | 942 | 1255 | 1753
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.045 | 522 | 878 | 1177 | 1630
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.05 | 482 | 820 | 1107 | 1521
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.055 | 448 | 768 | 1043 | 1425
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.06 | 417 | 721 | 984 | 1341
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.065 | 390 | 679 | 930 | 1265
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00481 | 0.00481 | 0.00291 | 0.00291 | 0.00291 | 0.83562 | 9.7108 | 271.872 | 0.07 | 365 | 640 | 881 | 1196
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.025 | 740 | 1176 | 1530 | 2215
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.03 | 672 | 1086 | 1426 | 2016
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.035 | 614 | 1007 | 1332 | 1855
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.04 | 563 | 935 | 1246 | 1717
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.045 | 518 | 871 | 1169 | 1599
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.05 | 479 | 814 | 1099 | 1495
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.055 | 444 | 762 | 1035 | 1403
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.06 | 413 | 715 | 977 | 1322
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.065 | 386 | 673 | 923 | 1248
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00476 | 0.00476 | 0.00291 | 0.00291 | 0.00291 | 0.84343 | 9.7561 | 271.872 | 0.07 | 362 | 635 | 874 | 1181

## 25%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.025 | 2755 | 11661 | 12182 | 12726
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.03 | 2622 | 9717 | 10151 | 10605
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.035 | 2498 | 8329 | 8701 | 9090
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.04 | 2383 | 7288 | 7614 | 7954
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.045 | 2274 | 6478 | 6768 | 7070
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.05 | 2173 | 5830 | 6091 | 6363
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.055 | 2078 | 5300 | 5537 | 5784
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.06 | 1990 | 4859 | 5076 | 5302
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.065 | 1906 | 4485 | 4685 | 4895
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00379 | 0.00251 | 0.00319 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00251 | 0.00251 | 0.47549 | 4.3678 | 185.472 | 0.07 | 1828 | 4165 | 4351 | 4545
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.025 | 2478 | 10593 | 11117 | 11667
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.03 | 2347 | 8827 | 9264 | 9723
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.035 | 2227 | 7566 | 7941 | 8334
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.04 | 2115 | 6621 | 6948 | 7292
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.045 | 2011 | 5885 | 6176 | 6482
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.05 | 1914 | 5296 | 5559 | 5834
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.055 | 1824 | 4815 | 5053 | 5303
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.06 | 1740 | 4414 | 4632 | 4861
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.065 | 1662 | 4074 | 4276 | 4487
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00315 | 0.00331 | 0.00788 | 0.00788 | 0.00251 | 0.00251 | 0.00251 | 0.47644 | 4.8324 | 185.472 | 0.07 | 1589 | 3783 | 3970 | 4167
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.025 | 2472 | 10571 | 11096 | 11646
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.03 | 2342 | 8810 | 9246 | 9705
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.035 | 2221 | 7551 | 7925 | 8318
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.04 | 2109 | 6607 | 6935 | 7279
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.045 | 2006 | 5873 | 6164 | 6470
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.05 | 1909 | 5286 | 5548 | 5823
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.055 | 1819 | 4805 | 5043 | 5294
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.06 | 1735 | 4405 | 4623 | 4852
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.065 | 1657 | 4066 | 4268 | 4479
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00328 | 0.00779 | 0.00779 | 0.00251 | 0.00251 | 0.00251 | 0.4778 | 4.8393 | 185.472 | 0.07 | 1585 | 3776 | 3963 | 4159
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.025 | 2467 | 10550 | 11074 | 11625
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.03 | 2337 | 8792 | 9229 | 9687
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.035 | 2216 | 7536 | 7910 | 8303
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.04 | 2104 | 6594 | 6921 | 7265
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.045 | 2000 | 5861 | 6152 | 6458
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.05 | 1904 | 5275 | 5537 | 5812
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.055 | 1814 | 4795 | 5034 | 5284
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.06 | 1731 | 4396 | 4614 | 4844
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.065 | 1653 | 4058 | 4259 | 4471
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00324 | 0.00769 | 0.00769 | 0.00251 | 0.00251 | 0.00251 | 0.47918 | 4.8463 | 185.472 | 0.07 | 1580 | 3768 | 3955 | 4152
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.025 | 2467 | 10550 | 11074 | 11625
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.03 | 2337 | 8792 | 9229 | 9687
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.035 | 2216 | 7536 | 7910 | 8303
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.04 | 2104 | 6594 | 6921 | 7265
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.045 | 2000 | 5861 | 6152 | 6458
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.05 | 1904 | 5275 | 5537 | 5812
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.055 | 1814 | 4795 | 5034 | 5284
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.06 | 1731 | 4396 | 4614 | 4844
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.065 | 1653 | 4058 | 4259 | 4471
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00306 | 0.0032 | 0.0076 | 0.0076 | 0.00251 | 0.00251 | 0.00251 | 0.48085 | 4.8547 | 185.472 | 0.07 | 1580 | 3768 | 3955 | 4152
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.025 | 2284 | 9770 | 10257 | 10767
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.03 | 2163 | 8142 | 8547 | 8973
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.035 | 2051 | 6979 | 7326 | 7691
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.04 | 1948 | 6106 | 6410 | 6730
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.045 | 1851 | 5428 | 5698 | 5982
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.05 | 1762 | 4885 | 5128 | 5384
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.055 | 1679 | 4441 | 4662 | 4894
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.06 | 1601 | 4071 | 4274 | 4486
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.065 | 1529 | 3758 | 3945 | 4141
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00293 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.4999 | 4.8645 | 199.872 | 0.07 | 1462 | 3489 | 3663 | 3846
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.025 | 2037 | 8782 | 9269 | 9783
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.03 | 1919 | 7318 | 7724 | 8153
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.035 | 1811 | 6273 | 6621 | 6988
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.04 | 1711 | 5488 | 5793 | 6114
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.045 | 1620 | 4879 | 5149 | 5435
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.05 | 1535 | 4391 | 4634 | 4892
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.055 | 1457 | 3992 | 4213 | 4447
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.06 | 1385 | 3659 | 3862 | 4076
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.065 | 1318 | 3378 | 3565 | 3763
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.50414 | 5.3993 | 199.872 | 0.07 | 1256 | 3136 | 3310 | 3494
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.025 | 2024 | 8731 | 9218 | 9733
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.03 | 1907 | 7276 | 7682 | 8110
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.035 | 1799 | 6236 | 6584 | 6952
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.04 | 1700 | 5457 | 5761 | 6083
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.045 | 1608 | 4851 | 5121 | 5407
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.05 | 1524 | 4365 | 4609 | 4866
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.055 | 1446 | 3969 | 4190 | 4424
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.06 | 1374 | 3638 | 3841 | 4055
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.065 | 1307 | 3358 | 3545 | 3743
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00288 | 0.0068 | 0.0068 | 0.00249 | 0.00249 | 0.00249 | 0.50968 | 5.4289 | 199.872 | 0.07 | 1245 | 3118 | 3292 | 3476
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.025 | 2012 | 8681 | 9168 | 9683
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.03 | 1895 | 7234 | 7640 | 8069
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.035 | 1787 | 6201 | 6549 | 6916
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.04 | 1688 | 5426 | 5730 | 6052
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.045 | 1597 | 4823 | 5093 | 5379
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.05 | 1513 | 4340 | 4584 | 4841
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.055 | 1435 | 3946 | 4167 | 4401
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.06 | 1363 | 3617 | 3820 | 4034
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.065 | 1297 | 3339 | 3526 | 3724
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.00271 | 0.00284 | 0.00672 | 0.00672 | 0.00249 | 0.00249 | 0.00249 | 0.51536 | 5.4591 | 199.872 | 0.07 | 1235 | 3100 | 3274 | 3458
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.025 | 1996 | 8615 | 9102 | 9616
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.03 | 1879 | 7179 | 7585 | 8014
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.035 | 1771 | 6153 | 6501 | 6869
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.04 | 1673 | 5384 | 5689 | 6010
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.045 | 1582 | 4786 | 5057 | 5342
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.05 | 1498 | 4307 | 4551 | 4808
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.055 | 1421 | 3916 | 4137 | 4371
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.06 | 1349 | 3589 | 3792 | 4007
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.065 | 1283 | 3313 | 3501 | 3699
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.0028 | 0.00664 | 0.00664 | 0.00249 | 0.00249 | 0.00249 | 0.52219 | 5.4952 | 199.872 | 0.07 | 1222 | 3077 | 3251 | 3434
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.025 | 1779 | 7694 | 8148 | 8628
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.03 | 1671 | 6412 | 6790 | 7190
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.035 | 1572 | 5496 | 5820 | 6163
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.04 | 1482 | 4809 | 5092 | 5393
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.045 | 1399 | 4274 | 4526 | 4793
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.05 | 1322 | 3847 | 4074 | 4314
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.055 | 1252 | 3497 | 3703 | 3922
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.06 | 1188 | 3206 | 3395 | 3595
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.065 | 1128 | 2959 | 3134 | 3319
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.0026 | 0.00616 | 0.00616 | 0.00247 | 0.00247 | 0.00247 | 0.59533 | 5.7299 | 214.272 | 0.07 | 1073 | 2748 | 2910 | 3081
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.025 | 1586 | 6395 | 7332 | 7812
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.03 | 1482 | 5362 | 6110 | 6510
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.035 | 1387 | 4620 | 5237 | 5580
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.04 | 1301 | 4060 | 4583 | 4882
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.045 | 1222 | 3622 | 4073 | 4340
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.05 | 1151 | 3270 | 3666 | 3906
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.055 | 1086 | 2981 | 3333 | 3551
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.06 | 1026 | 2739 | 3055 | 3255
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.065 | 971 | 2533 | 2820 | 3005
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00258 | 0.00609 | 0.00609 | 0.00247 | 0.00247 | 0.00247 | 0.59684 | 6.3411 | 214.272 | 0.07 | 921 | 2357 | 2619 | 2790
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.025 | 1584 | 6368 | 7320 | 7800
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.03 | 1479 | 5340 | 6100 | 6500
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.035 | 1384 | 4602 | 5228 | 5571
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.04 | 1298 | 4044 | 4575 | 4875
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.045 | 1220 | 3609 | 4066 | 4333
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.05 | 1148 | 3259 | 3660 | 3900
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.055 | 1083 | 2971 | 3327 | 3545
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.06 | 1023 | 2730 | 3050 | 3250
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.065 | 969 | 2525 | 2815 | 3000
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00254 | 0.00602 | 0.00602 | 0.00247 | 0.00247 | 0.00247 | 0.59864 | 6.3506 | 214.272 | 0.07 | 919 | 2349 | 2614 | 2786
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.025 | 1581 | 6341 | 7307 | 7787
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.03 | 1476 | 5318 | 6089 | 6489
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.035 | 1382 | 4584 | 5220 | 5562
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.04 | 1295 | 4029 | 4567 | 4867
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.045 | 1217 | 3596 | 4060 | 4326
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.05 | 1146 | 3247 | 3654 | 3894
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.055 | 1081 | 2961 | 3322 | 3540
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.06 | 1021 | 2720 | 3045 | 3245
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.065 | 966 | 2517 | 2811 | 2995
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00251 | 0.00595 | 0.00595 | 0.00247 | 0.00247 | 0.00247 | 0.60048 | 6.3604 | 214.272 | 0.07 | 916 | 2341 | 2610 | 2781
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.025 | 1578 | 6314 | 7295 | 7775
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.03 | 1474 | 5296 | 6079 | 6479
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.035 | 1379 | 4566 | 5211 | 5553
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.04 | 1293 | 4014 | 4559 | 4859
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.045 | 1215 | 3583 | 4053 | 4319
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.05 | 1143 | 3236 | 3647 | 3887
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.055 | 1078 | 2951 | 3316 | 3534
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.06 | 1019 | 2711 | 3040 | 3240
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.065 | 964 | 2509 | 2806 | 2990
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00284 | 0.00247 | 0.00247 | 0.00249 | 0.00589 | 0.00589 | 0.00247 | 0.00247 | 0.00247 | 0.60289 | 6.3732 | 214.272 | 0.07 | 914 | 2334 | 2605 | 2777
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.025 | 1503 | 6145 | 6940 | 7390
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.03 | 1405 | 5146 | 5784 | 6159
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.035 | 1315 | 4429 | 4957 | 5279
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.04 | 1234 | 3889 | 4338 | 4619
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.045 | 1160 | 3468 | 3856 | 4106
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.05 | 1093 | 3129 | 3470 | 3695
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.055 | 1031 | 2850 | 3155 | 3359
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.06 | 975 | 2618 | 2892 | 3079
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.065 | 923 | 2421 | 2669 | 2842
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.62138 | 6.2845 | 228.672 | 0.07 | 876 | 2250 | 2479 | 2639
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.025 | 1330 | 4362 | 6181 | 6628
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.03 | 1235 | 3723 | 5151 | 5523
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.035 | 1150 | 3256 | 4415 | 4734
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.04 | 1073 | 2897 | 3863 | 4143
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.045 | 1004 | 2611 | 3434 | 3682
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.05 | 941 | 2378 | 3091 | 3314
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.055 | 885 | 2184 | 2810 | 3013
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.06 | 833 | 2019 | 2576 | 2762
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.065 | 786 | 1878 | 2377 | 2549
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00545 | 0.00545 | 0.00245 | 0.00245 | 0.00245 | 0.62707 | 6.9777 | 228.672 | 0.07 | 743 | 1754 | 2208 | 2367
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.025 | 1321 | 4261 | 6119 | 6588
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.03 | 1226 | 3642 | 5101 | 5490
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.035 | 1141 | 3188 | 4375 | 4706
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.04 | 1065 | 2840 | 3829 | 4118
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.045 | 996 | 2563 | 3404 | 3660
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.05 | 934 | 2336 | 3065 | 3294
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.055 | 877 | 2146 | 2787 | 2995
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.06 | 826 | 1985 | 2554 | 2745
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.065 | 779 | 1846 | 2359 | 2534
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00259 | 0.00245 | 0.00245 | 0.00245 | 0.00539 | 0.00539 | 0.00245 | 0.00245 | 0.00245 | 0.63398 | 7.0161 | 228.672 | 0.07 | 737 | 1725 | 2190 | 2353
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.025 | 1312 | 4159 | 6036 | 6548
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.03 | 1218 | 3561 | 5036 | 5457
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.035 | 1133 | 3121 | 4322 | 4677
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.04 | 1057 | 2783 | 3785 | 4093
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.045 | 988 | 2514 | 3367 | 3638
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.05 | 926 | 2293 | 3032 | 3274
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.055 | 870 | 2108 | 2758 | 2977
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.06 | 819 | 1951 | 2529 | 2729
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.065 | 772 | 1815 | 2336 | 2519
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00532 | 0.00532 | 0.00245 | 0.00245 | 0.00245 | 0.64155 | 7.0578 | 228.672 | 0.07 | 730 | 1697 | 2169 | 2339
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.025 | 1301 | 4031 | 5932 | 6499
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.03 | 1207 | 3459 | 4954 | 5416
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.035 | 1123 | 3038 | 4255 | 4642
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.04 | 1047 | 2713 | 3730 | 4062
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.045 | 978 | 2452 | 3320 | 3611
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.05 | 917 | 2239 | 2992 | 3250
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.055 | 861 | 2060 | 2723 | 2954
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.06 | 810 | 1908 | 2498 | 2708
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.065 | 764 | 1777 | 2308 | 2500
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00526 | 0.00526 | 0.00245 | 0.00245 | 0.00245 | 0.65196 | 7.1149 | 228.672 | 0.07 | 722 | 1661 | 2144 | 2321
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.025 | 1242 | 4009 | 5757 | 6198
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.03 | 1154 | 3426 | 4799 | 5165
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.035 | 1074 | 2999 | 4115 | 4427
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.04 | 1002 | 2672 | 3602 | 3874
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.045 | 937 | 2410 | 3202 | 3443
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.05 | 878 | 2197 | 2883 | 3099
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.055 | 825 | 2019 | 2622 | 2817
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.06 | 777 | 1867 | 2403 | 2582
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.065 | 733 | 1737 | 2218 | 2384
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.67942 | 7.0217 | 243.072 | 0.07 | 693 | 1623 | 2060 | 2214
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.025 | 1097 | 2164 | 4248 | 5532
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.03 | 1012 | 1954 | 3617 | 4610
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.035 | 937 | 1785 | 3156 | 3952
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.04 | 869 | 1645 | 2804 | 3458
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.045 | 809 | 1525 | 2524 | 3073
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.05 | 755 | 1421 | 2297 | 2766
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.055 | 706 | 1329 | 2108 | 2515
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.06 | 662 | 1248 | 1947 | 2305
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.065 | 623 | 1175 | 1809 | 2128
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00491 | 0.00491 | 0.00244 | 0.00244 | 0.00244 | 0.68485 | 7.7918 | 243.072 | 0.07 | 587 | 1109 | 1690 | 1976
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.025 | 1090 | 2068 | 4170 | 5500
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.03 | 1006 | 1878 | 3555 | 4584
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.035 | 930 | 1722 | 3106 | 3929
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.04 | 863 | 1592 | 2763 | 3438
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.045 | 803 | 1479 | 2489 | 3056
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.05 | 749 | 1380 | 2266 | 2750
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.055 | 701 | 1293 | 2081 | 2500
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.06 | 657 | 1216 | 1923 | 2292
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.065 | 618 | 1146 | 1788 | 2116
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00486 | 0.00486 | 0.00244 | 0.00244 | 0.00244 | 0.69147 | 7.8293 | 243.072 | 0.07 | 582 | 1082 | 1670 | 1964
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.025 | 1084 | 1972 | 4091 | 5469
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.03 | 999 | 1801 | 3494 | 4557
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.035 | 924 | 1659 | 3056 | 3906
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.04 | 857 | 1538 | 2721 | 3418
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.045 | 797 | 1433 | 2454 | 3038
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.05 | 743 | 1340 | 2236 | 2734
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.055 | 695 | 1257 | 2054 | 2486
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.06 | 652 | 1184 | 1900 | 2279
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.065 | 613 | 1117 | 1767 | 2103
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.0048 | 0.0048 | 0.00244 | 0.00244 | 0.00244 | 0.69894 | 7.8715 | 243.072 | 0.07 | 578 | 1056 | 1651 | 1953
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.025 | 1074 | 1829 | 3974 | 5422
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.03 | 989 | 1687 | 3402 | 4518
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.035 | 915 | 1564 | 2982 | 3873
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.04 | 848 | 1458 | 2659 | 3389
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.045 | 788 | 1364 | 2401 | 3012
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.05 | 735 | 1280 | 2190 | 2711
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.055 | 687 | 1204 | 2014 | 2465
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.06 | 644 | 1135 | 1864 | 2259
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.065 | 606 | 1073 | 1735 | 2085
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00475 | 0.00475 | 0.00244 | 0.00244 | 0.00244 | 0.70867 | 7.9261 | 243.072 | 0.07 | 571 | 1016 | 1622 | 1936
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.025 | 1023 | 1862 | 3862 | 5163
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.03 | 943 | 1701 | 3298 | 4302
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.035 | 872 | 1567 | 2886 | 3688
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.04 | 809 | 1453 | 2569 | 3227
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.045 | 752 | 1353 | 2317 | 2868
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.05 | 702 | 1265 | 2111 | 2581
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.055 | 656 | 1187 | 1939 | 2347
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.06 | 616 | 1117 | 1793 | 2151
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.065 | 579 | 1055 | 1668 | 1986
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00452 | 0.00452 | 0.00243 | 0.00243 | 0.00243 | 0.75435 | 7.8733 | 257.472 | 0.07 | 545 | 997 | 1559 | 1844
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.025 | 885 | 1395 | 2050 | 3750
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.03 | 810 | 1297 | 1878 | 3212
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.035 | 744 | 1208 | 1733 | 2817
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.04 | 685 | 1128 | 1610 | 2513
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.045 | 634 | 1056 | 1502 | 2271
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.05 | 588 | 990 | 1407 | 2073
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.055 | 548 | 931 | 1322 | 1907
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.06 | 511 | 877 | 1245 | 1766
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.065 | 479 | 828 | 1176 | 1644
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00447 | 0.00447 | 0.00243 | 0.00243 | 0.00243 | 0.77938 | 8.8452 | 257.472 | 0.07 | 450 | 783 | 1113 | 1538
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.025 | 879 | 1386 | 1957 | 3673
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.03 | 804 | 1288 | 1805 | 3152
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.035 | 738 | 1199 | 1675 | 2770
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.04 | 680 | 1119 | 1561 | 2475
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.045 | 628 | 1047 | 1460 | 2239
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.05 | 583 | 982 | 1371 | 2046
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.055 | 543 | 923 | 1290 | 1884
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.06 | 507 | 869 | 1217 | 1746
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.065 | 475 | 821 | 1151 | 1626
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00443 | 0.00443 | 0.00243 | 0.00243 | 0.00243 | 0.78967 | 8.9035 | 257.472 | 0.07 | 446 | 776 | 1090 | 1522
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.025 | 876 | 1382 | 1920 | 3642
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.03 | 801 | 1284 | 1776 | 3129
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.035 | 735 | 1196 | 1651 | 2751
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.04 | 677 | 1116 | 1541 | 2460
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.045 | 626 | 1044 | 1444 | 2226
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.05 | 581 | 979 | 1356 | 2035
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.055 | 541 | 920 | 1277 | 1874
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.06 | 505 | 866 | 1206 | 1738
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.065 | 473 | 818 | 1141 | 1619
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00438 | 0.00438 | 0.00243 | 0.00243 | 0.00243 | 0.79197 | 8.9164 | 257.472 | 0.07 | 444 | 773 | 1081 | 1515
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.025 | 875 | 1380 | 1902 | 3626
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.03 | 800 | 1282 | 1762 | 3117
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.035 | 734 | 1194 | 1639 | 2742
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.04 | 676 | 1114 | 1531 | 2452
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.045 | 625 | 1042 | 1435 | 2220
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.05 | 580 | 977 | 1349 | 2029
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.055 | 540 | 918 | 1271 | 1870
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.06 | 504 | 865 | 1200 | 1733
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.065 | 472 | 816 | 1136 | 1615
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00433 | 0.00433 | 0.00243 | 0.00243 | 0.00243 | 0.79467 | 8.9316 | 257.472 | 0.07 | 443 | 772 | 1077 | 1512
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.025 | 865 | 1361 | 2327 | 3874
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.03 | 793 | 1266 | 2080 | 3290
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.035 | 729 | 1181 | 1886 | 2865
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.04 | 673 | 1105 | 1728 | 2541
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.045 | 623 | 1035 | 1595 | 2284
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.05 | 579 | 972 | 1482 | 2076
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.055 | 539 | 915 | 1383 | 1903
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.06 | 504 | 862 | 1296 | 1757
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.065 | 473 | 815 | 1219 | 1632
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00243 | 0.00243 | 0.00243 | 0.80673 | 8.6328 | 271.872 | 0.07 | 444 | 771 | 1149 | 1523
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.025 | 759 | 1204 | 1565 | 2494
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.03 | 691 | 1114 | 1460 | 2231
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.035 | 631 | 1033 | 1365 | 2024
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.04 | 579 | 961 | 1279 | 1855
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.045 | 534 | 896 | 1201 | 1715
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.05 | 494 | 837 | 1130 | 1593
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.055 | 458 | 785 | 1065 | 1487
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.06 | 427 | 737 | 1005 | 1395
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.065 | 399 | 694 | 951 | 1312
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0041 | 0.0041 | 0.00243 | 0.00243 | 0.00243 | 0.81168 | 9.5707 | 271.872 | 0.07 | 374 | 655 | 901 | 1238
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.025 | 756 | 1200 | 1559 | 2450
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.03 | 688 | 1109 | 1455 | 2197
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.035 | 628 | 1029 | 1360 | 1998
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.04 | 576 | 957 | 1274 | 1834
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.045 | 531 | 892 | 1196 | 1696
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.05 | 491 | 834 | 1125 | 1578
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.055 | 456 | 781 | 1060 | 1474
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.06 | 425 | 734 | 1001 | 1383
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.065 | 397 | 691 | 947 | 1302
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00243 | 0.00243 | 0.00243 | 0.81738 | 9.6043 | 271.872 | 0.07 | 372 | 652 | 897 | 1229
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.025 | 752 | 1194 | 1552 | 2391
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.03 | 684 | 1104 | 1447 | 2152
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.035 | 625 | 1023 | 1353 | 1962
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.04 | 573 | 951 | 1267 | 1804
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.045 | 528 | 887 | 1189 | 1672
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.05 | 488 | 829 | 1118 | 1557
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.055 | 453 | 776 | 1054 | 1456
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.06 | 422 | 729 | 995 | 1368
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.065 | 394 | 686 | 941 | 1288
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00401 | 0.00401 | 0.00243 | 0.00243 | 0.00243 | 0.8243 | 9.6449 | 271.872 | 0.07 | 370 | 648 | 891 | 1217
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.025 | 747 | 1186 | 1543 | 2318
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.03 | 679 | 1096 | 1438 | 2095
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.035 | 620 | 1016 | 1344 | 1917
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.04 | 569 | 944 | 1258 | 1768
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.045 | 524 | 880 | 1181 | 1642
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.05 | 484 | 822 | 1110 | 1531
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.055 | 449 | 770 | 1046 | 1434
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.06 | 418 | 723 | 987 | 1349
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.065 | 391 | 681 | 933 | 1271
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00396 | 0.00396 | 0.00243 | 0.00243 | 0.00243 | 0.83267 | 9.6937 | 271.872 | 0.07 | 366 | 642 | 884 | 1202

## 25%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.025 | 2789 | 11787 | 12307 | 12851
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.03 | 2656 | 9822 | 10256 | 10709
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.035 | 2531 | 8419 | 8791 | 9179
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.04 | 2415 | 7367 | 7692 | 8032
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.045 | 2306 | 6548 | 6837 | 7139
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.05 | 2205 | 5893 | 6154 | 6425
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.055 | 2109 | 5358 | 5594 | 5841
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.06 | 2020 | 4911 | 5128 | 5354
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.065 | 1936 | 4533 | 4734 | 4943
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00476 | 0.00991 | 0.00303 | 0.00201 | 0.00255 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00201 | 0.00201 | 0.46533 | 4.3209 | 185.472 | 0.07 | 1858 | 4210 | 4395 | 4589
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.025 | 2505 | 10702 | 11226 | 11775
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.03 | 2375 | 8918 | 9355 | 9813
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.035 | 2254 | 7644 | 8018 | 8411
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.04 | 2141 | 6688 | 7016 | 7359
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.045 | 2037 | 5945 | 6236 | 6542
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.05 | 1940 | 5351 | 5613 | 5888
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.055 | 1849 | 4864 | 5103 | 5352
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.06 | 1765 | 4459 | 4677 | 4906
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.065 | 1686 | 4116 | 4318 | 4529
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0057 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00252 | 0.00331 | 0.00788 | 0.00788 | 0.00201 | 0.00201 | 0.00201 | 0.46617 | 4.78 | 185.472 | 0.07 | 1613 | 3822 | 4009 | 4205
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.025 | 2500 | 10680 | 11204 | 11753
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.03 | 2369 | 8900 | 9336 | 9795
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.035 | 2248 | 7628 | 8003 | 8395
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.04 | 2136 | 6675 | 7002 | 7346
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.045 | 2032 | 5933 | 6224 | 6530
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.05 | 1935 | 5340 | 5602 | 5877
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.055 | 1844 | 4854 | 5093 | 5342
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.06 | 1760 | 4450 | 4668 | 4897
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.065 | 1682 | 4108 | 4309 | 4521
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00328 | 0.00779 | 0.00779 | 0.00201 | 0.00201 | 0.00201 | 0.4674 | 4.7864 | 185.472 | 0.07 | 1608 | 3814 | 4001 | 4198
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.025 | 2500 | 10680 | 11204 | 11753
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.03 | 2369 | 8900 | 9336 | 9795
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.035 | 2248 | 7628 | 8003 | 8395
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.04 | 2136 | 6675 | 7002 | 7346
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.045 | 2032 | 5933 | 6224 | 6530
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.05 | 1935 | 5340 | 5602 | 5877
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.055 | 1844 | 4854 | 5093 | 5342
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.06 | 1760 | 4450 | 4668 | 4897
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.065 | 1682 | 4108 | 4309 | 4521
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00463 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00324 | 0.00769 | 0.00769 | 0.00201 | 0.00201 | 0.00201 | 0.46866 | 4.7928 | 185.472 | 0.07 | 1608 | 3814 | 4001 | 4198
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.025 | 2494 | 10658 | 11182 | 11732
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.03 | 2364 | 8882 | 9318 | 9776
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.035 | 2243 | 7613 | 7987 | 8380
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.04 | 2131 | 6661 | 6989 | 7332
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.045 | 2026 | 5921 | 6212 | 6518
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.05 | 1929 | 5329 | 5591 | 5866
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.055 | 1839 | 4845 | 5083 | 5333
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.06 | 1755 | 4441 | 4659 | 4888
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.065 | 1677 | 4099 | 4301 | 4512
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00552 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00245 | 0.0032 | 0.0076 | 0.0076 | 0.00201 | 0.00201 | 0.00201 | 0.47019 | 4.8006 | 185.472 | 0.07 | 1603 | 3806 | 3994 | 4190
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.025 | 2309 | 9870 | 10356 | 10867
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.03 | 2189 | 8225 | 8630 | 9056
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.035 | 2076 | 7050 | 7397 | 7762
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.04 | 1972 | 6169 | 6473 | 6792
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.045 | 1876 | 5483 | 5754 | 6037
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.05 | 1786 | 4935 | 5178 | 5433
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.055 | 1702 | 4486 | 4707 | 4939
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.06 | 1624 | 4112 | 4315 | 4528
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.065 | 1551 | 3796 | 3983 | 4179
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00293 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.48821 | 4.8073 | 199.872 | 0.07 | 1484 | 3525 | 3699 | 3881
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.025 | 2062 | 8884 | 9371 | 9885
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.03 | 1944 | 7403 | 7809 | 8238
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.035 | 1835 | 6346 | 6694 | 7061
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.04 | 1735 | 5552 | 5857 | 6178
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.045 | 1643 | 4935 | 5206 | 5492
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.05 | 1558 | 4442 | 4686 | 4943
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.055 | 1479 | 4038 | 4260 | 4493
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.06 | 1406 | 3702 | 3905 | 4119
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.065 | 1339 | 3417 | 3604 | 3802
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.49233 | 5.3357 | 199.872 | 0.07 | 1276 | 3173 | 3347 | 3530
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.025 | 2049 | 8832 | 9320 | 9834
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.03 | 1931 | 7360 | 7766 | 8195
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.035 | 1823 | 6309 | 6657 | 7024
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.04 | 1723 | 5520 | 5825 | 6146
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.045 | 1631 | 4907 | 5178 | 5463
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.05 | 1546 | 4416 | 4660 | 4917
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.055 | 1468 | 4015 | 4236 | 4470
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.06 | 1395 | 3680 | 3883 | 4097
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.065 | 1328 | 3397 | 3585 | 3782
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00288 | 0.0068 | 0.0068 | 0.00199 | 0.00199 | 0.00199 | 0.49779 | 5.3652 | 199.872 | 0.07 | 1266 | 3154 | 3328 | 3512
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.025 | 2037 | 8782 | 9269 | 9783
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.03 | 1919 | 7318 | 7724 | 8153
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.035 | 1811 | 6273 | 6621 | 6988
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.04 | 1711 | 5488 | 5793 | 6114
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.045 | 1620 | 4879 | 5149 | 5435
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.05 | 1535 | 4391 | 4634 | 4892
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.055 | 1457 | 3992 | 4213 | 4447
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.06 | 1385 | 3659 | 3862 | 4076
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.065 | 1318 | 3378 | 3565 | 3763
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00217 | 0.00284 | 0.00672 | 0.00672 | 0.00199 | 0.00199 | 0.00199 | 0.50346 | 5.3957 | 199.872 | 0.07 | 1256 | 3136 | 3310 | 3494
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.025 | 2024 | 8731 | 9218 | 9733
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.03 | 1907 | 7276 | 7682 | 8110
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.035 | 1799 | 6236 | 6584 | 6952
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.04 | 1700 | 5457 | 5761 | 6083
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.045 | 1608 | 4851 | 5121 | 5407
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.05 | 1524 | 4365 | 4609 | 4866
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.055 | 1446 | 3969 | 4190 | 4424
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.06 | 1374 | 3638 | 3841 | 4055
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.065 | 1307 | 3358 | 3545 | 3743
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00483 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.0028 | 0.00664 | 0.00664 | 0.00199 | 0.00199 | 0.00199 | 0.51039 | 5.4327 | 199.872 | 0.07 | 1245 | 3118 | 3292 | 3476
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.025 | 1786 | 7723 | 8177 | 8657
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.03 | 1678 | 6436 | 6814 | 7214
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.035 | 1579 | 5516 | 5840 | 6184
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.04 | 1488 | 4827 | 5110 | 5411
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.045 | 1405 | 4290 | 4543 | 4809
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.05 | 1329 | 3861 | 4088 | 4329
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.055 | 1258 | 3510 | 3717 | 3935
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.06 | 1193 | 3218 | 3407 | 3607
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.065 | 1134 | 2970 | 3145 | 3330
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.0026 | 0.00616 | 0.00616 | 0.00198 | 0.00198 | 0.00198 | 0.59212 | 5.7144 | 214.272 | 0.07 | 1079 | 2758 | 2920 | 3092
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.025 | 1592 | 6449 | 7357 | 7837
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.03 | 1488 | 5405 | 6131 | 6531
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.035 | 1393 | 4656 | 5255 | 5598
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.04 | 1306 | 4090 | 4598 | 4898
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.045 | 1228 | 3648 | 4087 | 4354
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.05 | 1156 | 3293 | 3678 | 3918
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.055 | 1090 | 3002 | 3344 | 3562
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.06 | 1031 | 2757 | 3065 | 3265
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.065 | 976 | 2550 | 2830 | 3014
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00258 | 0.00609 | 0.00609 | 0.00198 | 0.00198 | 0.00198 | 0.59355 | 6.3236 | 214.272 | 0.07 | 925 | 2372 | 2627 | 2799
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.025 | 1589 | 6422 | 7344 | 7824
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.03 | 1485 | 5383 | 6120 | 6520
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.035 | 1390 | 4638 | 5246 | 5589
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.04 | 1304 | 4075 | 4590 | 4890
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.045 | 1225 | 3635 | 4080 | 4347
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.05 | 1153 | 3281 | 3672 | 3912
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.055 | 1088 | 2992 | 3338 | 3557
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.06 | 1028 | 2748 | 3060 | 3260
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.065 | 973 | 2542 | 2825 | 3009
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00254 | 0.00602 | 0.00602 | 0.00198 | 0.00198 | 0.00198 | 0.59526 | 6.3327 | 214.272 | 0.07 | 923 | 2364 | 2623 | 2794
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.025 | 1586 | 6395 | 7332 | 7812
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.03 | 1482 | 5362 | 6110 | 6510
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.035 | 1387 | 4620 | 5237 | 5580
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.04 | 1301 | 4060 | 4583 | 4882
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.045 | 1222 | 3622 | 4073 | 4340
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.05 | 1151 | 3270 | 3666 | 3906
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.055 | 1086 | 2981 | 3333 | 3551
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.06 | 1026 | 2739 | 3055 | 3255
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.065 | 971 | 2533 | 2820 | 3005
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00251 | 0.00595 | 0.00595 | 0.00198 | 0.00198 | 0.00198 | 0.59701 | 6.342 | 214.272 | 0.07 | 921 | 2357 | 2619 | 2790
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.025 | 1584 | 6368 | 7320 | 7800
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.03 | 1479 | 5340 | 6100 | 6500
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.035 | 1384 | 4602 | 5228 | 5571
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.04 | 1298 | 4044 | 4575 | 4875
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.045 | 1220 | 3609 | 4066 | 4333
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.05 | 1148 | 3259 | 3660 | 3900
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.055 | 1083 | 2971 | 3327 | 3545
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.06 | 1023 | 2730 | 3050 | 3250
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.065 | 969 | 2525 | 2815 | 3000
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00731 | 0.00227 | 0.00198 | 0.00198 | 0.00249 | 0.00589 | 0.00589 | 0.00198 | 0.00198 | 0.00198 | 0.59934 | 6.3543 | 214.272 | 0.07 | 919 | 2349 | 2614 | 2786
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.025 | 1508 | 6196 | 6964 | 7414
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.03 | 1410 | 5187 | 5803 | 6178
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.035 | 1321 | 4462 | 4974 | 5296
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.04 | 1239 | 3917 | 4353 | 4634
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.045 | 1165 | 3492 | 3869 | 4119
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.05 | 1098 | 3150 | 3482 | 3707
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.055 | 1036 | 2869 | 3165 | 3370
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.06 | 979 | 2635 | 2902 | 3089
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.065 | 927 | 2436 | 2678 | 2852
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.61748 | 6.2647 | 228.672 | 0.07 | 880 | 2265 | 2487 | 2648
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.025 | 1334 | 4413 | 6201 | 6648
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.03 | 1239 | 3764 | 5168 | 5540
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.035 | 1154 | 3289 | 4430 | 4749
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.04 | 1077 | 2925 | 3876 | 4155
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.045 | 1008 | 2636 | 3445 | 3694
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.05 | 945 | 2400 | 3101 | 3324
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.055 | 888 | 2203 | 2819 | 3022
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.06 | 837 | 2036 | 2584 | 2770
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.065 | 790 | 1893 | 2385 | 2557
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00328 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00545 | 0.00545 | 0.00196 | 0.00196 | 0.00196 | 0.62324 | 6.9564 | 228.672 | 0.07 | 747 | 1768 | 2215 | 2374
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.025 | 1325 | 4312 | 6161 | 6608
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.03 | 1231 | 3682 | 5134 | 5507
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.035 | 1146 | 3222 | 4401 | 4720
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.04 | 1069 | 2868 | 3851 | 4130
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.045 | 1000 | 2587 | 3423 | 3671
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.05 | 937 | 2357 | 3081 | 3304
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.055 | 881 | 2165 | 2801 | 3004
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.06 | 829 | 2002 | 2567 | 2753
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.065 | 783 | 1862 | 2370 | 2542
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00207 | 0.00196 | 0.00196 | 0.00245 | 0.00539 | 0.00539 | 0.00196 | 0.00196 | 0.00196 | 0.63034 | 6.9959 | 228.672 | 0.07 | 740 | 1740 | 2200 | 2360
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.025 | 1316 | 4210 | 6078 | 6568
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.03 | 1222 | 3601 | 5069 | 5474
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.035 | 1137 | 3155 | 4348 | 4692
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.04 | 1061 | 2812 | 3807 | 4105
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.045 | 992 | 2538 | 3386 | 3649
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.05 | 930 | 2314 | 3049 | 3284
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.055 | 873 | 2127 | 2773 | 2986
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.06 | 822 | 1968 | 2542 | 2737
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.065 | 776 | 1831 | 2347 | 2526
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00386 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00532 | 0.00532 | 0.00196 | 0.00196 | 0.00196 | 0.63829 | 7.0399 | 228.672 | 0.07 | 733 | 1711 | 2180 | 2346
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.025 | 1303 | 4057 | 5953 | 6509
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.03 | 1209 | 3479 | 4971 | 5424
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.035 | 1125 | 3054 | 4269 | 4649
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.04 | 1049 | 2727 | 3741 | 4068
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.045 | 980 | 2465 | 3329 | 3616
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.05 | 919 | 2250 | 3000 | 3255
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.055 | 863 | 2070 | 2730 | 2959
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.06 | 812 | 1917 | 2504 | 2712
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.065 | 766 | 1784 | 2314 | 2504
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00382 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00526 | 0.00526 | 0.00196 | 0.00196 | 0.00196 | 0.64959 | 7.102 | 228.672 | 0.07 | 724 | 1669 | 2149 | 2325
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.025 | 1242 | 4009 | 5757 | 6198
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.03 | 1154 | 3426 | 4799 | 5165
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.035 | 1074 | 2999 | 4115 | 4427
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.04 | 1002 | 2672 | 3602 | 3874
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.045 | 937 | 2410 | 3202 | 3443
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.05 | 878 | 2197 | 2883 | 3099
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.055 | 825 | 2019 | 2622 | 2817
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.06 | 777 | 1867 | 2403 | 2582
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.065 | 733 | 1737 | 2218 | 2384
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.67942 | 7.0217 | 243.072 | 0.07 | 693 | 1623 | 2060 | 2214
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.025 | 1097 | 2164 | 4248 | 5532
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.03 | 1012 | 1954 | 3617 | 4610
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.035 | 937 | 1785 | 3156 | 3952
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.04 | 869 | 1645 | 2804 | 3458
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.045 | 809 | 1525 | 2524 | 3073
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.05 | 755 | 1421 | 2297 | 2766
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.055 | 706 | 1329 | 2108 | 2515
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.06 | 662 | 1248 | 1947 | 2305
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.065 | 623 | 1175 | 1809 | 2128
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00491 | 0.00491 | 0.00195 | 0.00195 | 0.00195 | 0.68485 | 7.7918 | 243.072 | 0.07 | 587 | 1109 | 1690 | 1976
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.025 | 1090 | 2068 | 4170 | 5500
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.03 | 1006 | 1878 | 3555 | 4584
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.035 | 930 | 1722 | 3106 | 3929
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.04 | 863 | 1592 | 2763 | 3438
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.045 | 803 | 1479 | 2489 | 3056
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.05 | 749 | 1380 | 2266 | 2750
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.055 | 701 | 1293 | 2081 | 2500
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.06 | 657 | 1216 | 1923 | 2292
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.065 | 618 | 1146 | 1788 | 2116
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00486 | 0.00486 | 0.00195 | 0.00195 | 0.00195 | 0.69147 | 7.8293 | 243.072 | 0.07 | 582 | 1082 | 1670 | 1964
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.025 | 1084 | 1972 | 4091 | 5469
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.03 | 999 | 1801 | 3494 | 4557
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.035 | 924 | 1659 | 3056 | 3906
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.04 | 857 | 1538 | 2721 | 3418
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.045 | 797 | 1433 | 2454 | 3038
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.05 | 743 | 1340 | 2236 | 2734
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.055 | 695 | 1257 | 2054 | 2486
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.06 | 652 | 1184 | 1900 | 2279
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.065 | 613 | 1117 | 1767 | 2103
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.0048 | 0.0048 | 0.00195 | 0.00195 | 0.00195 | 0.69894 | 7.8715 | 243.072 | 0.07 | 578 | 1056 | 1651 | 1953
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.025 | 1074 | 1829 | 3974 | 5422
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.03 | 989 | 1687 | 3402 | 4518
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.035 | 915 | 1564 | 2982 | 3873
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.04 | 848 | 1458 | 2659 | 3389
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.045 | 788 | 1364 | 2401 | 3012
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.05 | 735 | 1280 | 2190 | 2711
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.055 | 687 | 1204 | 2014 | 2465
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.06 | 644 | 1135 | 1864 | 2259
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.065 | 606 | 1073 | 1735 | 2085
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00346 | 0.00289 | 0.00593 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00475 | 0.00475 | 0.00195 | 0.00195 | 0.00195 | 0.70867 | 7.9261 | 243.072 | 0.07 | 571 | 1016 | 1622 | 1936
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.025 | 1023 | 1862 | 3862 | 5163
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.03 | 943 | 1701 | 3298 | 4302
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.035 | 872 | 1567 | 2886 | 3688
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.04 | 809 | 1453 | 2569 | 3227
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.045 | 752 | 1353 | 2317 | 2868
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.05 | 702 | 1265 | 2111 | 2581
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.055 | 656 | 1187 | 1939 | 2347
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.06 | 616 | 1117 | 1793 | 2151
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.065 | 579 | 1055 | 1668 | 1986
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.00561 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.75435 | 7.8733 | 257.472 | 0.07 | 545 | 997 | 1559 | 1844
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.025 | 885 | 1395 | 2050 | 3750
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.03 | 810 | 1297 | 1878 | 3212
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.035 | 744 | 1208 | 1733 | 2817
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.04 | 685 | 1128 | 1610 | 2513
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.045 | 634 | 1056 | 1502 | 2271
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.05 | 588 | 990 | 1407 | 2073
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.055 | 548 | 931 | 1322 | 1907
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.06 | 511 | 877 | 1245 | 1766
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.065 | 479 | 828 | 1176 | 1644
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.77938 | 8.8452 | 257.472 | 0.07 | 450 | 783 | 1113 | 1538
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.025 | 879 | 1386 | 1957 | 3673
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.03 | 804 | 1288 | 1805 | 3152
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.035 | 738 | 1199 | 1675 | 2770
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.04 | 680 | 1119 | 1561 | 2475
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.045 | 628 | 1047 | 1460 | 2239
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.05 | 583 | 982 | 1371 | 2046
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.055 | 543 | 923 | 1290 | 1884
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.06 | 507 | 869 | 1217 | 1746
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.065 | 475 | 821 | 1151 | 1626
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00269 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.78967 | 8.9035 | 257.472 | 0.07 | 446 | 776 | 1090 | 1522
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.025 | 876 | 1382 | 1920 | 3642
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.03 | 801 | 1284 | 1776 | 3129
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.035 | 735 | 1196 | 1651 | 2751
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.04 | 677 | 1116 | 1541 | 2460
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.045 | 626 | 1044 | 1444 | 2226
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.05 | 581 | 979 | 1356 | 2035
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.055 | 541 | 920 | 1277 | 1874
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.06 | 505 | 866 | 1206 | 1738
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.065 | 473 | 818 | 1141 | 1619
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.79197 | 8.9164 | 257.472 | 0.07 | 444 | 773 | 1081 | 1515
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.025 | 875 | 1380 | 1902 | 3626
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.03 | 800 | 1282 | 1762 | 3117
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.035 | 734 | 1194 | 1639 | 2742
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.04 | 676 | 1114 | 1531 | 2452
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.045 | 625 | 1042 | 1435 | 2220
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.05 | 580 | 977 | 1349 | 2029
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.055 | 540 | 918 | 1271 | 1870
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.06 | 504 | 865 | 1200 | 1733
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.065 | 472 | 816 | 1136 | 1615
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00433 | 0.00433 | 0.00194 | 0.00194 | 0.00194 | 0.79467 | 8.9316 | 257.472 | 0.07 | 443 | 772 | 1077 | 1512
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.025 | 865 | 1361 | 2327 | 3874
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.03 | 793 | 1266 | 2080 | 3290
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.035 | 729 | 1181 | 1886 | 2865
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.04 | 673 | 1105 | 1728 | 2541
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.045 | 623 | 1035 | 1595 | 2284
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.05 | 579 | 972 | 1482 | 2076
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.055 | 539 | 915 | 1383 | 1903
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.06 | 504 | 862 | 1296 | 1757
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.065 | 473 | 815 | 1219 | 1632
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00303 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00194 | 0.00194 | 0.00194 | 0.80673 | 8.6328 | 271.872 | 0.07 | 444 | 771 | 1149 | 1523
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.025 | 759 | 1204 | 1565 | 2494
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.03 | 691 | 1114 | 1460 | 2231
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.035 | 631 | 1033 | 1365 | 2024
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.04 | 579 | 961 | 1279 | 1855
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.045 | 534 | 896 | 1201 | 1715
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.05 | 494 | 837 | 1130 | 1593
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.055 | 458 | 785 | 1065 | 1487
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.06 | 427 | 737 | 1005 | 1395
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.065 | 399 | 694 | 951 | 1312
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0041 | 0.0041 | 0.00194 | 0.00194 | 0.00194 | 0.81168 | 9.5707 | 271.872 | 0.07 | 374 | 655 | 901 | 1238
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.025 | 756 | 1200 | 1559 | 2450
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.03 | 688 | 1109 | 1455 | 2197
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.035 | 628 | 1029 | 1360 | 1998
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.04 | 576 | 957 | 1274 | 1834
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.045 | 531 | 892 | 1196 | 1696
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.05 | 491 | 834 | 1125 | 1578
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.055 | 456 | 781 | 1060 | 1474
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.06 | 425 | 734 | 1001 | 1383
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.065 | 397 | 691 | 947 | 1302
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00194 | 0.00194 | 0.00194 | 0.81738 | 9.6043 | 271.872 | 0.07 | 372 | 652 | 897 | 1229
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.025 | 752 | 1194 | 1552 | 2391
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.03 | 684 | 1104 | 1447 | 2152
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.035 | 625 | 1023 | 1353 | 1962
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.04 | 573 | 951 | 1267 | 1804
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.045 | 528 | 887 | 1189 | 1672
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.05 | 488 | 829 | 1118 | 1557
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.055 | 453 | 776 | 1054 | 1456
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.06 | 422 | 729 | 995 | 1368
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.065 | 394 | 686 | 941 | 1288
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00401 | 0.00401 | 0.00194 | 0.00194 | 0.00194 | 0.8243 | 9.6449 | 271.872 | 0.07 | 370 | 648 | 891 | 1217
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.025 | 747 | 1186 | 1543 | 2318
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.03 | 679 | 1096 | 1438 | 2095
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.035 | 620 | 1016 | 1344 | 1917
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.04 | 569 | 944 | 1258 | 1768
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.045 | 524 | 880 | 1181 | 1642
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.05 | 484 | 822 | 1110 | 1531
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.055 | 449 | 770 | 1046 | 1434
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.06 | 418 | 723 | 987 | 1349
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.065 | 391 | 681 | 933 | 1271
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00396 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.83267 | 9.6937 | 271.872 | 0.07 | 366 | 642 | 884 | 1202

## 50%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.025 | 2736 | 11586 | 12107 | 12652
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.03 | 2603 | 9655 | 10089 | 10543
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.035 | 2479 | 8276 | 8648 | 9037
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.04 | 2364 | 7241 | 7567 | 7907
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.045 | 2256 | 6437 | 6726 | 7029
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.05 | 2155 | 5793 | 6054 | 6326
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.055 | 2060 | 5266 | 5503 | 5751
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.06 | 1972 | 4828 | 5045 | 5272
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.065 | 1889 | 4456 | 4657 | 4866
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00571 | 0.01189 | 0.00303 | 0.00201 | 0.00255 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00201 | 0.00201 | 0.48255 | 4.4001 | 185.472 | 0.07 | 1811 | 4138 | 4324 | 4519
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.025 | 2456 | 10507 | 11032 | 11582
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00684 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00252 | 0.00398 | 0.00945 | 0.00945 | 0.00201 | 0.00201 | 0.00201 | 0.48333 | 4.8672 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.025 | 2456 | 10507 | 11032 | 11582
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.03 | 2326 | 8756 | 9193 | 9652
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.035 | 2205 | 7505 | 7880 | 8273
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.04 | 2094 | 6567 | 6895 | 7239
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.045 | 1990 | 5837 | 6129 | 6435
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.05 | 1894 | 5254 | 5516 | 5791
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.055 | 1804 | 4776 | 5014 | 5265
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.06 | 1721 | 4378 | 4596 | 4826
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.065 | 1643 | 4041 | 4243 | 4455
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00393 | 0.00935 | 0.00935 | 0.00201 | 0.00201 | 0.00201 | 0.48453 | 4.8733 | 185.472 | 0.07 | 1571 | 3753 | 3940 | 4136
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.025 | 2450 | 10486 | 11010 | 11561
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.03 | 2320 | 8738 | 9175 | 9634
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.035 | 2200 | 7490 | 7865 | 8258
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.04 | 2089 | 6554 | 6881 | 7226
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.045 | 1985 | 5826 | 6117 | 6423
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.05 | 1889 | 5243 | 5505 | 5781
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.055 | 1799 | 4766 | 5005 | 5255
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.06 | 1716 | 4369 | 4588 | 4817
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.065 | 1639 | 4033 | 4235 | 4447
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00555 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00388 | 0.00923 | 0.00923 | 0.00201 | 0.00201 | 0.00201 | 0.48574 | 4.8793 | 185.472 | 0.07 | 1566 | 3745 | 3932 | 4129
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.025 | 2445 | 10465 | 10989 | 11540
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.03 | 2315 | 8721 | 9158 | 9617
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.035 | 2195 | 7475 | 7849 | 8243
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.04 | 2083 | 6540 | 6868 | 7212
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.045 | 1980 | 5814 | 6105 | 6411
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.05 | 1884 | 5232 | 5495 | 5770
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.055 | 1794 | 4757 | 4995 | 5245
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.06 | 1711 | 4360 | 4579 | 4808
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.065 | 1634 | 4025 | 4227 | 4438
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00663 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00245 | 0.00384 | 0.00912 | 0.00912 | 0.00201 | 0.00201 | 0.00201 | 0.48722 | 4.8868 | 185.472 | 0.07 | 1562 | 3737 | 3925 | 4121
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.025 | 2269 | 9711 | 10198 | 10709
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.03 | 2148 | 8092 | 8498 | 8924
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.035 | 2037 | 6936 | 7284 | 7649
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.04 | 1933 | 6069 | 6373 | 6693
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.045 | 1837 | 5395 | 5665 | 5949
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.05 | 1748 | 4855 | 5099 | 5354
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.055 | 1665 | 4414 | 4635 | 4868
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.06 | 1588 | 4046 | 4249 | 4462
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.065 | 1516 | 3735 | 3922 | 4119
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00351 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.50517 | 4.8901 | 199.872 | 0.07 | 1449 | 3468 | 3642 | 3825
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.025 | 2024 | 8731 | 9218 | 9733
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.03 | 1907 | 7276 | 7682 | 8110
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.035 | 1799 | 6236 | 6584 | 6952
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.04 | 1700 | 5457 | 5761 | 6083
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.045 | 1608 | 4851 | 5121 | 5407
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.05 | 1524 | 4365 | 4609 | 4866
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.055 | 1446 | 3969 | 4190 | 4424
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.06 | 1374 | 3638 | 3841 | 4055
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.065 | 1307 | 3358 | 3545 | 3743
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.5093 | 5.4269 | 199.872 | 0.07 | 1245 | 3118 | 3292 | 3476
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.025 | 2012 | 8681 | 9168 | 9683
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.03 | 1895 | 7234 | 7640 | 8069
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.035 | 1787 | 6201 | 6549 | 6916
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.04 | 1688 | 5426 | 5730 | 6052
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.045 | 1597 | 4823 | 5093 | 5379
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.05 | 1513 | 4340 | 4584 | 4841
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.055 | 1435 | 3946 | 4167 | 4401
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.06 | 1363 | 3617 | 3820 | 4034
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.065 | 1297 | 3339 | 3526 | 3724
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00345 | 0.00816 | 0.00816 | 0.00199 | 0.00199 | 0.00199 | 0.51476 | 5.4559 | 199.872 | 0.07 | 1235 | 3100 | 3274 | 3458
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.025 | 2000 | 8631 | 9118 | 9633
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.03 | 1883 | 7193 | 7599 | 8027
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.035 | 1775 | 6165 | 6513 | 6881
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.04 | 1676 | 5395 | 5699 | 6021
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.045 | 1585 | 4795 | 5066 | 5352
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.05 | 1502 | 4316 | 4559 | 4816
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.055 | 1424 | 3923 | 4145 | 4379
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.06 | 1353 | 3596 | 3799 | 4014
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.065 | 1287 | 3320 | 3507 | 3705
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00217 | 0.00341 | 0.00807 | 0.00807 | 0.00199 | 0.00199 | 0.00199 | 0.52042 | 5.4858 | 199.872 | 0.07 | 1225 | 3083 | 3257 | 3440
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.025 | 1988 | 8582 | 9069 | 9584
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.03 | 1871 | 7152 | 7557 | 7986
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.035 | 1764 | 6130 | 6478 | 6845
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.04 | 1665 | 5364 | 5668 | 5990
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.045 | 1574 | 4768 | 5038 | 5324
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.05 | 1491 | 4291 | 4534 | 4792
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.055 | 1414 | 3901 | 4122 | 4356
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.06 | 1342 | 3576 | 3779 | 3993
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.065 | 1277 | 3301 | 3488 | 3686
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00579 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00336 | 0.00796 | 0.00796 | 0.00199 | 0.00199 | 0.00199 | 0.52733 | 5.5222 | 199.872 | 0.07 | 1216 | 3065 | 3239 | 3423
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.025 | 1755 | 7594 | 8047 | 8528
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.03 | 1647 | 6328 | 6706 | 7107
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.035 | 1549 | 5424 | 5748 | 6091
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.04 | 1459 | 4746 | 5030 | 5330
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.045 | 1376 | 4219 | 4471 | 4738
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.05 | 1301 | 3797 | 4024 | 4264
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.055 | 1231 | 3452 | 3658 | 3876
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.06 | 1167 | 3164 | 3353 | 3553
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.065 | 1108 | 2921 | 3095 | 3280
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00312 | 0.0074 | 0.0074 | 0.00198 | 0.00198 | 0.00198 | 0.60922 | 5.7964 | 214.272 | 0.07 | 1054 | 2712 | 2874 | 3046
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.025 | 1567 | 6205 | 7246 | 7726
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.03 | 1462 | 5210 | 6038 | 6438
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.035 | 1368 | 4495 | 5176 | 5518
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.04 | 1282 | 3954 | 4529 | 4829
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.045 | 1204 | 3531 | 4026 | 4292
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.05 | 1133 | 3190 | 3623 | 3863
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.055 | 1069 | 2910 | 3294 | 3512
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.06 | 1009 | 2675 | 3019 | 3219
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.065 | 955 | 2476 | 2787 | 2971
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00309 | 0.00731 | 0.00731 | 0.00198 | 0.00198 | 0.00198 | 0.61068 | 6.4142 | 214.272 | 0.07 | 905 | 2304 | 2588 | 2759
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.025 | 1564 | 6178 | 7234 | 7714
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.03 | 1460 | 5188 | 6028 | 6428
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.035 | 1365 | 4477 | 5167 | 5510
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.04 | 1280 | 3939 | 4521 | 4821
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.045 | 1202 | 3518 | 4019 | 4285
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.05 | 1131 | 3179 | 3617 | 3857
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.055 | 1066 | 2900 | 3288 | 3506
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.06 | 1007 | 2666 | 3014 | 3214
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.065 | 953 | 2467 | 2782 | 2967
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00305 | 0.00723 | 0.00723 | 0.00198 | 0.00198 | 0.00198 | 0.61243 | 6.4234 | 214.272 | 0.07 | 903 | 2296 | 2584 | 2755
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.025 | 1561 | 6150 | 7222 | 7701
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.03 | 1457 | 5166 | 6018 | 6418
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.035 | 1363 | 4459 | 5158 | 5501
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.04 | 1277 | 3923 | 4514 | 4813
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.045 | 1199 | 3505 | 4012 | 4279
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.05 | 1128 | 3167 | 3611 | 3851
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.055 | 1064 | 2890 | 3283 | 3501
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.06 | 1005 | 2657 | 3009 | 3209
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.065 | 951 | 2459 | 2778 | 2962
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00302 | 0.00714 | 0.00714 | 0.00198 | 0.00198 | 0.00198 | 0.61423 | 6.4328 | 214.272 | 0.07 | 901 | 2288 | 2579 | 2750
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.025 | 1555 | 6096 | 7198 | 7677
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.03 | 1451 | 5123 | 5998 | 6398
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.035 | 1357 | 4423 | 5141 | 5484
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.04 | 1272 | 3893 | 4499 | 4798
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.045 | 1194 | 3479 | 3999 | 4265
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.05 | 1124 | 3144 | 3599 | 3839
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.055 | 1059 | 2870 | 3272 | 3490
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.06 | 1000 | 2638 | 2999 | 3199
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.065 | 946 | 2442 | 2768 | 2953
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00877 | 0.00227 | 0.00198 | 0.00198 | 0.00298 | 0.00706 | 0.00706 | 0.00198 | 0.00198 | 0.00198 | 0.61663 | 6.4454 | 214.272 | 0.07 | 897 | 2273 | 2571 | 2742
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.025 | 1484 | 5967 | 6859 | 7308
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.03 | 1386 | 5004 | 5716 | 6090
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.035 | 1297 | 4311 | 4899 | 5220
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.04 | 1216 | 3790 | 4287 | 4568
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.045 | 1143 | 3382 | 3810 | 4060
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.05 | 1076 | 3054 | 3429 | 3654
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.055 | 1015 | 2784 | 3118 | 3322
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.06 | 959 | 2558 | 2858 | 3045
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.065 | 908 | 2366 | 2638 | 2811
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00662 | 0.00662 | 0.00196 | 0.00196 | 0.00196 | 0.63532 | 6.3546 | 228.672 | 0.07 | 861 | 2201 | 2450 | 2610
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.025 | 1312 | 4159 | 6036 | 6548
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.03 | 1218 | 3561 | 5036 | 5457
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.035 | 1133 | 3121 | 4322 | 4677
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.04 | 1057 | 2783 | 3785 | 4093
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.045 | 988 | 2514 | 3367 | 3638
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.05 | 926 | 2293 | 3032 | 3274
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.055 | 870 | 2108 | 2758 | 2977
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.06 | 819 | 1951 | 2529 | 2729
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.065 | 772 | 1815 | 2336 | 2519
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00393 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00654 | 0.00654 | 0.00196 | 0.00196 | 0.00196 | 0.64121 | 7.056 | 228.672 | 0.07 | 730 | 1697 | 2169 | 2339
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.025 | 1303 | 4057 | 5953 | 6509
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.03 | 1209 | 3479 | 4971 | 5424
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.035 | 1125 | 3054 | 4269 | 4649
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.04 | 1049 | 2727 | 3741 | 4068
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.045 | 980 | 2465 | 3329 | 3616
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.05 | 919 | 2250 | 3000 | 3255
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.055 | 863 | 2070 | 2730 | 2959
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.06 | 812 | 1917 | 2504 | 2712
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.065 | 766 | 1784 | 2314 | 2504
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00207 | 0.00196 | 0.00196 | 0.00294 | 0.00646 | 0.00646 | 0.00196 | 0.00196 | 0.00196 | 0.64846 | 7.0957 | 228.672 | 0.07 | 724 | 1669 | 2149 | 2325
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.025 | 1295 | 3955 | 5869 | 6470
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.03 | 1201 | 3398 | 4905 | 5392
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.035 | 1117 | 2987 | 4216 | 4622
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.04 | 1041 | 2670 | 3697 | 4044
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.045 | 973 | 2416 | 3292 | 3595
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.05 | 911 | 2207 | 2968 | 3235
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.055 | 855 | 2032 | 2702 | 2941
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.06 | 805 | 1882 | 2479 | 2696
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.065 | 759 | 1753 | 2291 | 2489
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00464 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00639 | 0.00639 | 0.00196 | 0.00196 | 0.00196 | 0.65655 | 7.1399 | 228.672 | 0.07 | 717 | 1640 | 2128 | 2311
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.025 | 1282 | 3802 | 5744 | 6412
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.03 | 1188 | 3276 | 4808 | 5344
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.035 | 1105 | 2887 | 4136 | 4580
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.04 | 1029 | 2585 | 3631 | 4008
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.045 | 961 | 2342 | 3236 | 3562
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.05 | 900 | 2143 | 2919 | 3206
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.055 | 845 | 1975 | 2659 | 2915
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.06 | 795 | 1831 | 2441 | 2672
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.065 | 749 | 1707 | 2257 | 2466
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00459 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00632 | 0.00632 | 0.00196 | 0.00196 | 0.00196 | 0.66802 | 7.2019 | 228.672 | 0.07 | 708 | 1598 | 2098 | 2290
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.025 | 1222 | 3769 | 5561 | 6105
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.03 | 1134 | 3235 | 4646 | 5088
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.035 | 1054 | 2842 | 3991 | 4361
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.04 | 983 | 2538 | 3499 | 3816
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.045 | 919 | 2295 | 3114 | 3392
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.05 | 861 | 2096 | 2807 | 3053
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.055 | 808 | 1929 | 2555 | 2775
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.06 | 760 | 1787 | 2344 | 2544
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.065 | 717 | 1664 | 2165 | 2348
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.69848 | 7.1195 | 243.072 | 0.07 | 678 | 1556 | 2012 | 2180
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.025 | 1079 | 1901 | 4032 | 5445
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.03 | 994 | 1744 | 3448 | 4538
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.035 | 919 | 1612 | 3019 | 3890
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.04 | 852 | 1498 | 2690 | 3403
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.045 | 793 | 1398 | 2428 | 3025
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.05 | 739 | 1310 | 2213 | 2723
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.055 | 691 | 1231 | 2034 | 2475
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.06 | 648 | 1159 | 1882 | 2269
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.065 | 609 | 1095 | 1751 | 2094
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00357 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0059 | 0.0059 | 0.00195 | 0.00195 | 0.00195 | 0.70402 | 7.9001 | 243.072 | 0.07 | 574 | 1036 | 1637 | 1945
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.025 | 1072 | 1805 | 3954 | 5414
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.03 | 988 | 1668 | 3386 | 4512
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.035 | 913 | 1549 | 2969 | 3867
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.04 | 846 | 1445 | 2649 | 3384
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.045 | 787 | 1352 | 2392 | 3008
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.05 | 734 | 1270 | 2183 | 2707
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.055 | 686 | 1195 | 2008 | 2461
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.06 | 643 | 1127 | 1858 | 2256
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.065 | 604 | 1066 | 1729 | 2082
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00583 | 0.00583 | 0.00195 | 0.00195 | 0.00195 | 0.71071 | 7.9375 | 243.072 | 0.07 | 569 | 1009 | 1617 | 1934
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.025 | 1066 | 1709 | 3876 | 5383
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.03 | 982 | 1591 | 3325 | 4486
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.035 | 907 | 1486 | 2919 | 3845
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.04 | 840 | 1392 | 2607 | 3365
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.045 | 781 | 1306 | 2357 | 2991
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.05 | 728 | 1229 | 2152 | 2692
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.055 | 681 | 1159 | 1981 | 2447
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.06 | 638 | 1095 | 1834 | 2243
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.065 | 600 | 1037 | 1708 | 2071
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00576 | 0.00576 | 0.00195 | 0.00195 | 0.00195 | 0.71818 | 7.9791 | 243.072 | 0.07 | 565 | 982 | 1598 | 1923
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.025 | 1058 | 1654 | 3778 | 5319
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.03 | 974 | 1546 | 3248 | 4435
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.035 | 899 | 1447 | 2857 | 3804
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.04 | 833 | 1358 | 2555 | 3331
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.045 | 774 | 1277 | 2313 | 2962
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.05 | 722 | 1203 | 2114 | 2667
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.055 | 674 | 1135 | 1947 | 2425
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.06 | 632 | 1073 | 1805 | 2224
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.065 | 594 | 1016 | 1682 | 2054
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00416 | 0.00347 | 0.00711 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.0057 | 0.0057 | 0.00195 | 0.00195 | 0.00195 | 0.72774 | 8.032 | 243.072 | 0.07 | 559 | 964 | 1574 | 1907
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.025 | 1009 | 1658 | 3696 | 5097
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.03 | 930 | 1538 | 3168 | 4247
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.035 | 859 | 1433 | 2780 | 3641
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.04 | 796 | 1339 | 2481 | 3186
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.045 | 740 | 1255 | 2242 | 2832
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.05 | 690 | 1179 | 2046 | 2548
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.055 | 645 | 1111 | 1882 | 2317
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.06 | 605 | 1048 | 1743 | 2124
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.065 | 568 | 993 | 1623 | 1960
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00673 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.77072 | 7.9582 | 257.472 | 0.07 | 535 | 940 | 1518 | 1820
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.025 | 876 | 1382 | 1920 | 3642
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.03 | 801 | 1284 | 1776 | 3129
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.035 | 735 | 1196 | 1651 | 2751
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.04 | 677 | 1116 | 1541 | 2460
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.045 | 626 | 1044 | 1444 | 2226
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.05 | 581 | 979 | 1356 | 2035
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.055 | 541 | 920 | 1277 | 1874
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.06 | 505 | 866 | 1206 | 1738
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.065 | 473 | 818 | 1141 | 1619
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.79273 | 8.9207 | 257.472 | 0.07 | 444 | 773 | 1081 | 1515
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.025 | 870 | 1373 | 1827 | 3564
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.03 | 795 | 1275 | 1703 | 3069
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.035 | 730 | 1187 | 1592 | 2704
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.04 | 672 | 1108 | 1492 | 2421
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.045 | 621 | 1036 | 1402 | 2194
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.05 | 576 | 971 | 1321 | 2008
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.055 | 536 | 912 | 1246 | 1851
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.06 | 501 | 859 | 1178 | 1717
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.065 | 469 | 811 | 1116 | 1601
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00323 | 0.00658 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.80171 | 8.9711 | 257.472 | 0.07 | 440 | 766 | 1059 | 1499
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.025 | 869 | 1371 | 1809 | 3549
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.03 | 794 | 1273 | 1689 | 3057
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.035 | 729 | 1185 | 1581 | 2694
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.04 | 671 | 1106 | 1483 | 2413
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.045 | 620 | 1034 | 1394 | 2188
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.05 | 575 | 970 | 1313 | 2002
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.055 | 535 | 911 | 1240 | 1846
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.06 | 500 | 858 | 1172 | 1713
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.065 | 468 | 809 | 1111 | 1597
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.80403 | 8.984 | 257.472 | 0.07 | 439 | 765 | 1054 | 1496
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.025 | 867 | 1368 | 1772 | 3518
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.03 | 792 | 1270 | 1660 | 3034
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.035 | 726 | 1182 | 1557 | 2676
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.04 | 669 | 1103 | 1463 | 2398
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.045 | 618 | 1031 | 1377 | 2175
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.05 | 573 | 967 | 1299 | 1992
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.055 | 533 | 908 | 1227 | 1837
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.06 | 498 | 855 | 1161 | 1705
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.065 | 466 | 807 | 1101 | 1590
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00519 | 0.00519 | 0.00194 | 0.00194 | 0.00194 | 0.80675 | 8.9992 | 257.472 | 0.07 | 438 | 762 | 1045 | 1490
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.025 | 856 | 1348 | 2204 | 3771
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.03 | 784 | 1254 | 1984 | 3211
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.035 | 721 | 1169 | 1808 | 2802
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.04 | 665 | 1093 | 1663 | 2490
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.045 | 616 | 1024 | 1540 | 2242
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.05 | 572 | 961 | 1434 | 2040
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.055 | 533 | 904 | 1341 | 1872
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.06 | 498 | 852 | 1259 | 1730
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.065 | 467 | 805 | 1186 | 1608
| 36 | 32 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00363 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00194 | 0.00194 | 0.00194 | 0.81874 | 8.6968 | 271.872 | 0.07 | 438 | 761 | 1119 | 1502
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.025 | 752 | 1194 | 1552 | 2391
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.03 | 684 | 1104 | 1447 | 2152
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.035 | 625 | 1023 | 1353 | 1962
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.04 | 573 | 951 | 1267 | 1804
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.045 | 528 | 887 | 1189 | 1672
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.05 | 488 | 829 | 1118 | 1557
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.055 | 453 | 776 | 1054 | 1456
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.06 | 422 | 729 | 995 | 1368
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.065 | 394 | 686 | 941 | 1288
| 36 | 32 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00492 | 0.00492 | 0.00194 | 0.00194 | 0.00194 | 0.82355 | 9.6405 | 271.872 | 0.07 | 370 | 648 | 891 | 1217
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.025 | 749 | 1189 | 1546 | 2347
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.03 | 681 | 1099 | 1442 | 2118
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.035 | 622 | 1019 | 1347 | 1935
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.04 | 570 | 947 | 1262 | 1783
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.045 | 525 | 883 | 1184 | 1654
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.05 | 486 | 825 | 1113 | 1542
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.055 | 451 | 773 | 1049 | 1443
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.06 | 420 | 726 | 990 | 1356
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.065 | 392 | 683 | 936 | 1278
| 36 | 32 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00194 | 0.00194 | 0.00194 | 0.82904 | 9.6726 | 271.872 | 0.07 | 368 | 644 | 887 | 1208
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.025 | 745 | 1183 | 1539 | 2289
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.03 | 677 | 1094 | 1435 | 2073
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.035 | 618 | 1013 | 1340 | 1899
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.04 | 567 | 942 | 1255 | 1753
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.045 | 522 | 878 | 1177 | 1630
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.05 | 482 | 820 | 1107 | 1521
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.055 | 448 | 768 | 1043 | 1425
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.06 | 417 | 721 | 984 | 1341
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.065 | 390 | 679 | 930 | 1265
| 36 | 32 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00481 | 0.00481 | 0.00194 | 0.00194 | 0.00194 | 0.83562 | 9.7108 | 271.872 | 0.07 | 365 | 640 | 881 | 1196
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.025 | 740 | 1176 | 1530 | 2215
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.03 | 672 | 1086 | 1426 | 2016
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.035 | 614 | 1007 | 1332 | 1855
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.04 | 563 | 935 | 1246 | 1717
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.045 | 518 | 871 | 1169 | 1599
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.05 | 479 | 814 | 1099 | 1495
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.055 | 444 | 762 | 1035 | 1403
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.06 | 413 | 715 | 977 | 1322
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.065 | 386 | 673 | 923 | 1248
| 36 | 32 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00476 | 0.00476 | 0.00194 | 0.00194 | 0.00194 | 0.84343 | 9.7561 | 271.872 | 0.07 | 362 | 635 | 874 | 1181