## Slab_Properties
References:
Slab properties: |  |  | bay type
l1 = | 36 | ft | exterior | * must be larger span |  |  |  | CRSI Design Guide for Vibration of Reinforced Concrete Floor Systems, First Edition
l2 = | 16 | ft | interior |  |  |  |  | ACI 318-14 Building Code Requirements for Structural Concrete
l1 / l2 = |  |  | * must be < 2.0, otherwise exhibits one way behavior |  |  |  |  | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
c1 = | 24 | in
c2 = | 24 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = |  | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 12 | in
d = |  | in | *single layer of reinforcement
wc = | 150 | pcf
yt = |  | in
n =
lcw = |  |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = |  | psi | * reduced modulus of rupture, per CRSI Design Guide p4-6
Strip widths
Direction | Column | Middle
l1 |  |  | ft | * needs to be adjusted for exterior spans?
l2 |  |  | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = |  | psf
mass = |  | lb sec2/ft
weight = |  | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = |  |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = |  | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = |  | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = |  | k-ft
M1n1u = |  | k-ft
M1n2u = |  | k-ft
M2pu = |  | k-ft
M2n1u = |  | k-ft
M2n2u = |  | k-ft
Service Moments
M01,DL = |  | k-ft | *includes SDL and self-weight
M01,LL = |  | k-ft
M02,DL = |  | k-ft
M02,LL = |  | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p |  |  | k-ft
l1 | DL | n1 |  |  | k-ft
l1 | DL | n2 |  |  | k-ft
l1 | LL | p |  |  | k-ft
l1 | LL | n1 |  |  | k-ft
l1 | LL | n2 |  |  | k-ft
l2 | DL | p |  |  | k-ft
l2 | DL | n1 |  |  | k-ft
l2 | DL | n2 |  |  | k-ft
l2 | LL | p |  |  | k-ft
l2 | LL | n1 |  |  | k-ft
l2 | LL | n2 |  |  | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p |  |  | k-ft
l1 | n1 |  |  | k-ft
l1 | n2 |  |  | k-ft
l2 | p |  |  | k-ft
l2 | n1 |  |  | k-ft
l2 | n2 |  |  | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation (may be unconservative… ): | [6 empty] | User input (As from rho): |  |  |  |  | User input (rho):
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle
l1 | p |  |  | in2 | l1 | p |  |  | in2 | l1 | p |  |  |  | l1 | p | 0.00461 | 0.00303
l1 | n1 |  |  | in2 | l1 | n1 |  |  | in2 | l1 | n1 |  |  |  | l1 | n1 | 0.00382 | 0.00201
l1 | n2 |  |  | in2 | l1 | n2 |  |  | in2 | l1 | n2 |  |  |  | l1 | n2 | 0.00794 | 0.00255
l2 | p |  |  | in2 | l2 | p |  |  | in2 | l2 | p |  |  |  | l2 | p | 0.00201 | 0.00201
l2 | n1 |  |  | in2 | l2 | n1 |  |  | in2 | l2 | n1 |  |  |  | l2 | n1 | 0.00271 | 0.00201
l2 | n2 |  |  | in2 | l2 | n2 |  |  | in2 | l2 | n2 |  |  |  | l2 | n2 | 0.00271 | 0.00201
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p |  |  | in3
l1 | n1 |  |  | in3
l1 | n2 |  |  | in3
l2 | p |  |  | in3
l2 | n1 |  |  | in3
l2 | n2 |  |  | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p |  |  | in3
l1 | n1 |  |  | in3
l1 | n2 |  |  | in3
l2 | p |  |  | in3
l2 | n1 |  |  | in3
l2 | n2 |  |  | in3
Calculate avg strip Ie
Direction | Column | Middle
l1 |  |  | in3
l2 |  |  | in3
Calculate Panel Ie
Iep = |  | in3
Calculate Panel Ig
Igp = |  | in3
Calculate k1
k1 =
Calculate fi |  |  | Interp li2
k2 = |  |  | 1 | 7.12
li2 = |  |  | 1.5 | 8.92
g = |  | slug / ft2 | 2 | 9.29
fi = |  | Hz
Calculate/Input Parameters for DG11
W = |  | lb
b = | 0.03

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits | [7 empty] | References:
fn= |  | Hz | [5 empty] | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
W = |  | lb
b =
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips | Velocity
Very Slow |  | 1.25 | - | - | - | - | - |  | - |  | - |  | mips
Slow |  | 1.6 | 6.8 | 6 | 8 | 0.1 | [6 empty] | mips | * does not consider mode scaling
Moderate |  | 1.85 | 8 | 7 | 9 | 0.09 | [6 empty] | mips
Fast |  | 2.1 | 8.8 | 8 | 10 | 0.08 | [6 empty] | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201
2 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201
3 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201
4 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201
5 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201
6 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199
7 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199
8 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199
9 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199
10 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199
11 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198
12 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198
13 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198
14 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198
15 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198
16 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196
17 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196
18 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196
19 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196
20 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196
21 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195
22 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195
23 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195
24 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195
25 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195
26 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194
27 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194
28 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194
29 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194
30 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194
31 | 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193
32 | 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193
33 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193
34 | 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193
35 | 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193

## Drop_panel_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | hdrop | heff | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | *Assumes drop panels are 1/6 length of span in each direction
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | in | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 |  |  | 150 | 0 | 80 | 11
2 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 16 |  | 150 | 0 | 80 | 11
3 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 17 |  | 150 | 0 | 80 | 11
4 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 |  |  | 150 | 0 | 80 | 11
5 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 17 |  | 150 | 0 | 80 | 11
6 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 18 |  | 150 | 0 | 80 | 11
7 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 |  |  | 150 | 0 | 80 | 11
8 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 18 |  | 150 | 0 | 80 | 11
9 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 19 |  | 150 | 0 | 80 | 11
10 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 12 |  | 150 | 0 | 80 | 11
11 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 13 |  | 150 | 0 | 80 | 11
12 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 |  | 150 | 0 | 80 | 11
13 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 |  | 150 | 0 | 80 | 11
14 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 15 |  | 150 | 0 | 80 | 11
15 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 16 |  | 150 | 0 | 80 | 11
16 | 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 17 |  | 150 | 0 | 80 | 11

## thickness_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11

## exterior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.03 | 3245 | 10940 | 13457 | 14379
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.035 | 3030 | 9480 | 11534 | 12325
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.04 | 2836 | 8371 | 10092 | 10784
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.045 | 2659 | 7499 | 8971 | 9586
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.05 | 2499 | 6793 | 8074 | 8627
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.055 | 2353 | 6210 | 7340 | 7843
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.06 | 2220 | 5720 | 6728 | 7190
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.065 | 2098 | 5301 | 6211 | 6636
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00461 | 0.00382 | 0.00794 | 0.00303 | 0.00201 | 0.00255 | 0.00201 | 0.00271 | 0.00271 | 0.00201 | 0.00201 | 0.00201 | 0.7278 | 6.6316 | 92.736 | 0.07 | 1987 | 4940 | 5767 | 6162
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.03 | 2867 | 7431 | 11338 | 12930
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.035 | 2662 | 6585 | 9780 | 11083
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.045 | 2313 | 5387 | 7683 | 8620
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.05 | 2164 | 4942 | 6941 | 7758
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.055 | 2030 | 4566 | 6332 | 7053
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.06 | 1908 | 4243 | 5821 | 6465
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.065 | 1798 | 3961 | 5386 | 5968
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00455 | 0.00377 | 0.00785 | 0.003 | 0.00201 | 0.00253 | 0.00201 | 0.00265 | 0.00265 | 0.00201 | 0.00201 | 0.00201 | 0.72761 | 7.3287 | 92.736 | 0.07 | 1698 | 3714 | 5012 | 5542
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.03 | 2867 | 7431 | 11338 | 12930
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.035 | 2662 | 6585 | 9780 | 11083
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.045 | 2313 | 5387 | 7683 | 8620
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.05 | 2164 | 4942 | 6941 | 7758
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.055 | 2030 | 4566 | 6332 | 7053
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.06 | 1908 | 4243 | 5821 | 6465
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.065 | 1798 | 3961 | 5386 | 5968
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.07 | 1698 | 3714 | 5012 | 5542
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.03 | 2867 | 7431 | 11338 | 12930
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.035 | 2662 | 6585 | 9780 | 11083
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.045 | 2313 | 5387 | 7683 | 8620
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.05 | 2164 | 4942 | 6941 | 7758
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.055 | 2030 | 4566 | 6332 | 7053
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.06 | 1908 | 4243 | 5821 | 6465
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.065 | 1798 | 3961 | 5386 | 5968
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00447 | 0.00369 | 0.00769 | 0.00295 | 0.00201 | 0.00247 | 0.00201 | 0.00252 | 0.00252 | 0.00201 | 0.00201 | 0.00201 | 0.72744 | 7.3279 | 92.736 | 0.07 | 1698 | 3714 | 5012 | 5542
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.03 | 2867 | 7431 | 11338 | 12930
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.035 | 2662 | 6585 | 9780 | 11083
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.045 | 2313 | 5387 | 7683 | 8620
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.05 | 2164 | 4942 | 6941 | 7758
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.055 | 2030 | 4566 | 6332 | 7053
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.06 | 1908 | 4243 | 5821 | 6465
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.065 | 1798 | 3961 | 5386 | 5968
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00443 | 0.00366 | 0.00761 | 0.00292 | 0.00201 | 0.00244 | 0.00201 | 0.00245 | 0.00245 | 0.00201 | 0.00201 | 0.00201 | 0.72739 | 7.3276 | 92.736 | 0.07 | 1698 | 3714 | 5012 | 5542
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.03 | 2720 | 7500 | 11006 | 12233
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.035 | 2529 | 6609 | 9469 | 10485
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.04 | 2356 | 5917 | 8312 | 9175
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.045 | 2201 | 5363 | 7407 | 8155
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.05 | 2061 | 4905 | 6682 | 7340
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.055 | 1934 | 4521 | 6086 | 6673
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.06 | 1819 | 4191 | 5589 | 6116
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.065 | 1715 | 3907 | 5166 | 5646
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.00691 | 0.00266 | 0.00199 | 0.00223 | 0.00199 | 0.00238 | 0.00238 | 0.00199 | 0.00199 | 0.00199 | 0.72692 | 7.1989 | 99.936 | 0.07 | 1620 | 3658 | 4804 | 5243
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.03 | 2396 | 3964 | 8166 | 10948
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.035 | 2214 | 3692 | 7165 | 9384
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.045 | 1908 | 3235 | 5779 | 7299
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.05 | 1779 | 3040 | 5275 | 6569
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.055 | 1663 | 2864 | 4852 | 5972
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.06 | 1559 | 2703 | 4493 | 5474
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.065 | 1465 | 2557 | 4183 | 5053
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00398 | 0.0033 | 0.00684 | 0.00263 | 0.00199 | 0.00221 | 0.00199 | 0.00231 | 0.00231 | 0.00199 | 0.00199 | 0.00199 | 0.72693 | 7.9567 | 99.936 | 0.07 | 1380 | 2424 | 3913 | 4692
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.03 | 2396 | 3964 | 8166 | 10948
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.035 | 2214 | 3692 | 7165 | 9384
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.045 | 1908 | 3235 | 5779 | 7299
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.05 | 1779 | 3040 | 5275 | 6569
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.055 | 1663 | 2864 | 4852 | 5972
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.06 | 1559 | 2703 | 4493 | 5474
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.065 | 1465 | 2557 | 4183 | 5053
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.07 | 1380 | 2424 | 3913 | 4692
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.03 | 2396 | 3964 | 8166 | 10948
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.035 | 2214 | 3692 | 7165 | 9384
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.045 | 1908 | 3235 | 5779 | 7299
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.05 | 1779 | 3040 | 5275 | 6569
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.055 | 1663 | 2864 | 4852 | 5972
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.06 | 1559 | 2703 | 4493 | 5474
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.065 | 1465 | 2557 | 4183 | 5053
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0039 | 0.00324 | 0.0067 | 0.00258 | 0.00199 | 0.00216 | 0.00199 | 0.00221 | 0.00221 | 0.00199 | 0.00199 | 0.00199 | 0.72722 | 7.9583 | 99.936 | 0.07 | 1380 | 2424 | 3913 | 4692
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.03 | 2396 | 3964 | 8166 | 10948
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.035 | 2214 | 3692 | 7165 | 9384
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.045 | 1908 | 3235 | 5779 | 7299
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.05 | 1779 | 3040 | 5275 | 6569
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.055 | 1663 | 2864 | 4852 | 5972
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.06 | 1559 | 2703 | 4493 | 5474
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.065 | 1465 | 2557 | 4183 | 5053
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00387 | 0.0032 | 0.00663 | 0.00255 | 0.00199 | 0.00215 | 0.00199 | 0.00215 | 0.00215 | 0.00199 | 0.00199 | 0.00199 | 0.72746 | 7.9596 | 99.936 | 0.07 | 1380 | 2424 | 3913 | 4692
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.03 | 2301 | 4479 | 8244 | 10479
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.035 | 2130 | 4088 | 7193 | 8982
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.04 | 1976 | 3764 | 6388 | 7859
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.045 | 1839 | 3487 | 5750 | 6986
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.05 | 1716 | 3248 | 5231 | 6288
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.055 | 1606 | 3037 | 4799 | 5716
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.06 | 1507 | 2851 | 4433 | 5240
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.065 | 1417 | 2683 | 4119 | 4837
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.0061 | 0.00236 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00211 | 0.00198 | 0.00198 | 0.00198 | 0.72784 | 7.7751 | 107.136 | 0.07 | 1336 | 2533 | 3846 | 4491
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.03 | 2022 | 3229 | 5385 | 8438
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.035 | 1860 | 3013 | 4874 | 7341
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.045 | 1590 | 2640 | 4111 | 5845
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.05 | 1477 | 2480 | 3814 | 5310
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.055 | 1377 | 2334 | 3557 | 4866
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.06 | 1287 | 2201 | 3330 | 4490
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.065 | 1207 | 2079 | 3130 | 4168
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00352 | 0.00293 | 0.00604 | 0.00234 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00206 | 0.00198 | 0.00198 | 0.00198 | 0.72827 | 8.5961 | 107.136 | 0.07 | 1135 | 1968 | 2950 | 3890
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.03 | 2022 | 3229 | 5385 | 8438
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.035 | 1860 | 3013 | 4874 | 7341
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.045 | 1590 | 2640 | 4111 | 5845
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.05 | 1477 | 2480 | 3814 | 5310
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.055 | 1377 | 2334 | 3557 | 4866
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.06 | 1287 | 2201 | 3330 | 4490
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.065 | 1207 | 2079 | 3130 | 4168
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.07 | 1135 | 1968 | 2950 | 3890
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.03 | 2022 | 3229 | 5385 | 8438
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.035 | 1860 | 3013 | 4874 | 7341
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.045 | 1590 | 2640 | 4111 | 5845
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.05 | 1477 | 2480 | 3814 | 5310
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.055 | 1377 | 2334 | 3557 | 4866
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.06 | 1287 | 2201 | 3330 | 4490
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.065 | 1207 | 2079 | 3130 | 4168
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.00592 | 0.00229 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.72955 | 8.6037 | 107.136 | 0.07 | 1135 | 1968 | 2950 | 3890
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.03 | 2019 | 3224 | 5350 | 8409
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.035 | 1857 | 3008 | 4846 | 7318
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.04 | 1714 | 2813 | 4435 | 6487
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.045 | 1587 | 2636 | 4091 | 5830
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.05 | 1475 | 2475 | 3797 | 5297
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.055 | 1374 | 2330 | 3542 | 4854
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.06 | 1285 | 2197 | 3317 | 4480
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.065 | 1205 | 2075 | 3118 | 4159
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00342 | 0.00284 | 0.00586 | 0.00227 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.00198 | 0.73064 | 8.6101 | 107.136 | 0.07 | 1132 | 1965 | 2939 | 3882
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.03 | 1963 | 3127 | 5797 | 8522
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.035 | 1808 | 2922 | 5176 | 7368
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.04 | 1672 | 2736 | 4685 | 6495
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.045 | 1550 | 2567 | 4283 | 5809
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.05 | 1442 | 2414 | 3946 | 5257
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.055 | 1346 | 2274 | 3659 | 4801
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.06 | 1259 | 2147 | 3411 | 4418
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.065 | 1181 | 2030 | 3193 | 4092
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00546 | 0.00211 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7324 | 8.3731 | 114.336 | 0.07 | 1112 | 1923 | 3000 | 3811
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.03 | 1717 | 2761 | 3614 | 6137
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.035 | 1573 | 2566 | 3385 | 5474
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.04 | 1446 | 2390 | 3176 | 4952
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.045 | 1334 | 2232 | 2987 | 4525
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.05 | 1236 | 2090 | 2813 | 4169
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.055 | 1149 | 1961 | 2655 | 3864
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.06 | 1071 | 1844 | 2510 | 3602
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.065 | 1002 | 1739 | 2377 | 3372
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00541 | 0.00209 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73389 | 9.2638 | 114.336 | 0.07 | 940 | 1642 | 2255 | 3169
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.03 | 1712 | 2754 | 3604 | 6084
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.035 | 1568 | 2559 | 3376 | 5432
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.04 | 1441 | 2383 | 3168 | 4917
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.045 | 1330 | 2226 | 2978 | 4497
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.05 | 1232 | 2083 | 2805 | 4144
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.055 | 1145 | 1955 | 2647 | 3843
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.06 | 1067 | 1838 | 2502 | 3583
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.065 | 999 | 1733 | 2370 | 3355
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.07 | 937 | 1637 | 2248 | 3154
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.03 | 1710 | 2750 | 3600 | 6057
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.035 | 1565 | 2555 | 3371 | 5411
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.04 | 1439 | 2380 | 3163 | 4900
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.045 | 1328 | 2222 | 2974 | 4482
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.05 | 1230 | 2080 | 2801 | 4132
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.055 | 1143 | 1952 | 2643 | 3833
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.06 | 1066 | 1835 | 2498 | 3574
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.065 | 997 | 1730 | 2366 | 3347
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0031 | 0.00258 | 0.0053 | 0.00205 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73808 | 9.2903 | 114.336 | 0.07 | 935 | 1634 | 2244 | 3147
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.03 | 1705 | 2743 | 3590 | 6003
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.035 | 1561 | 2548 | 3362 | 5368
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.04 | 1434 | 2373 | 3154 | 4865
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.045 | 1323 | 2216 | 2965 | 4453
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.05 | 1225 | 2074 | 2792 | 4108
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.055 | 1139 | 1945 | 2635 | 3812
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.06 | 1062 | 1829 | 2490 | 3556
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.065 | 993 | 1724 | 2358 | 3331
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00307 | 0.00255 | 0.00524 | 0.00203 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.74111 | 9.3093 | 114.336 | 0.07 | 932 | 1628 | 2237 | 3133
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.03 | 1671 | 2680 | 3503 | 6353
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.035 | 1532 | 2494 | 3286 | 5610
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.04 | 1411 | 2326 | 3087 | 5034
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.045 | 1303 | 2175 | 2906 | 4569
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.05 | 1209 | 2039 | 2740 | 4186
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.055 | 1124 | 1915 | 2589 | 3863
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.06 | 1049 | 1803 | 2450 | 3587
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.065 | 983 | 1701 | 2322 | 3347
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00289 | 0.0024 | 0.00493 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.74556 | 9.0268 | 121.536 | 0.07 | 923 | 1607 | 2204 | 3137
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.03 | 1454 | 2354 | 3093 | 3903
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.035 | 1325 | 2178 | 2885 | 3665
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.04 | 1213 | 2021 | 2697 | 3447
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.045 | 1115 | 1880 | 2527 | 3249
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.05 | 1029 | 1754 | 2373 | 3066
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.055 | 954 | 1641 | 2232 | 2899
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.06 | 888 | 1539 | 2105 | 2746
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.065 | 829 | 1447 | 1988 | 2605
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00286 | 0.00237 | 0.00488 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75018 | 10.0079 | 121.536 | 0.07 | 776 | 1364 | 1882 | 2475
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.03 | 1446 | 2343 | 3078 | 3884
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.035 | 1317 | 2166 | 2871 | 3647
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.04 | 1205 | 2010 | 2683 | 3430
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.045 | 1108 | 1869 | 2513 | 3231
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.05 | 1023 | 1744 | 2359 | 3050
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.055 | 948 | 1631 | 2219 | 2883
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.06 | 882 | 1530 | 2092 | 2730
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.065 | 823 | 1438 | 1976 | 2590
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.07 | 771 | 1355 | 1870 | 2460
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.03 | 1434 | 2325 | 3056 | 3857
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.035 | 1306 | 2149 | 2849 | 3620
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.04 | 1195 | 1993 | 2662 | 3404
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.045 | 1098 | 1853 | 2493 | 3206
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.05 | 1013 | 1729 | 2339 | 3025
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.055 | 939 | 1616 | 2200 | 2859
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.06 | 873 | 1516 | 2073 | 2707
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.065 | 815 | 1425 | 1958 | 2567
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0028 | 0.00233 | 0.00478 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76632 | 10.1149 | 121.536 | 0.07 | 763 | 1342 | 1853 | 2438
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.03 | 1411 | 2290 | 3012 | 3803
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.035 | 1284 | 2116 | 2806 | 3567
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.04 | 1174 | 1960 | 2620 | 3352
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.045 | 1078 | 1822 | 2452 | 3156
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.05 | 994 | 1698 | 2300 | 2976
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.055 | 921 | 1588 | 2162 | 2812
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.06 | 856 | 1488 | 2037 | 2661
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.065 | 799 | 1398 | 1923 | 2522
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00278 | 0.0023 | 0.00473 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78409 | 10.2315 | 121.536 | 0.07 | 748 | 1317 | 1819 | 2395
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.03 | 1409 | 2278 | 2990 | 4117
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.035 | 1285 | 2109 | 2791 | 3804
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.04 | 1178 | 1959 | 2612 | 3536
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.045 | 1084 | 1824 | 2449 | 3302
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.05 | 1001 | 1704 | 2301 | 3094
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.055 | 929 | 1595 | 2167 | 2909
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.06 | 865 | 1497 | 2044 | 2743
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.065 | 808 | 1408 | 1932 | 2592
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00263 | 0.00219 | 0.00448 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.77866 | 9.8166 | 128.736 | 0.07 | 757 | 1328 | 1830 | 2455
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.03 | 1210 | 1977 | 2610 | 3305
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.035 | 1096 | 1819 | 2422 | 3089
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.04 | 998 | 1679 | 2253 | 2893
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.045 | 914 | 1556 | 2102 | 2715
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.05 | 841 | 1446 | 1966 | 2553
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.055 | 777 | 1348 | 1843 | 2405
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.06 | 721 | 1260 | 1732 | 2271
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.065 | 671 | 1182 | 1631 | 2147
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00261 | 0.00217 | 0.00444 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79469 | 10.9611 | 128.736 | 0.07 | 628 | 1111 | 1540 | 2035
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.03 | 1207 | 1972 | 2604 | 3298
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.035 | 1093 | 1814 | 2416 | 3082
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.04 | 996 | 1675 | 2248 | 2886
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.045 | 911 | 1551 | 2097 | 2708
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.05 | 838 | 1442 | 1961 | 2546
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.055 | 774 | 1344 | 1838 | 2399
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.06 | 719 | 1257 | 1727 | 2264
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.065 | 669 | 1178 | 1627 | 2142
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.07 | 626 | 1108 | 1536 | 2029
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.03 | 1204 | 1967 | 2598 | 3291
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.035 | 1090 | 1810 | 2410 | 3075
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.04 | 993 | 1671 | 2242 | 2879
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.045 | 909 | 1547 | 2091 | 2701
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.05 | 836 | 1438 | 1956 | 2540
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.055 | 772 | 1340 | 1833 | 2393
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.06 | 716 | 1253 | 1722 | 2258
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.065 | 667 | 1175 | 1622 | 2136
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79971 | 10.9956 | 128.736 | 0.07 | 624 | 1104 | 1531 | 2023
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.03 | 1202 | 1965 | 2595 | 3287
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.035 | 1089 | 1807 | 2407 | 3071
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.04 | 992 | 1668 | 2239 | 2876
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.045 | 908 | 1545 | 2089 | 2698
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.05 | 835 | 1436 | 1953 | 2537
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.055 | 771 | 1338 | 1831 | 2390
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.06 | 715 | 1251 | 1720 | 2255
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.065 | 666 | 1173 | 1620 | 2133
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.00431 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80175 | 11.0097 | 128.736 | 0.07 | 623 | 1103 | 1529 | 2020
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.03 | 1196 | 1948 | 2568 | 3248
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.035 | 1086 | 1796 | 2387 | 3040
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.04 | 991 | 1661 | 2225 | 2852
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.045 | 908 | 1541 | 2078 | 2680
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.05 | 836 | 1434 | 1946 | 2523
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.055 | 774 | 1338 | 1827 | 2380
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.06 | 718 | 1253 | 1719 | 2249
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.065 | 670 | 1176 | 1620 | 2130
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00241 | 0.00201 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8118 | 10.6275 | 135.936 | 0.07 | 626 | 1106 | 1531 | 2020
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.03 | 1034 | 1701 | 2255 | 2865
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.035 | 933 | 1559 | 2084 | 2667
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.04 | 846 | 1433 | 1932 | 2489
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.045 | 772 | 1323 | 1796 | 2328
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.05 | 708 | 1226 | 1674 | 2182
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.055 | 653 | 1140 | 1565 | 2050
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.06 | 604 | 1063 | 1467 | 1930
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.065 | 562 | 995 | 1379 | 1821
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00407 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.81623 | 11.7782 | 135.936 | 0.07 | 525 | 934 | 1299 | 1722
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.03 | 1030 | 1696 | 2248 | 2856
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.035 | 929 | 1553 | 2077 | 2659
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.04 | 843 | 1428 | 1925 | 2480
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.045 | 769 | 1318 | 1789 | 2320
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.05 | 705 | 1221 | 1668 | 2174
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.055 | 650 | 1135 | 1559 | 2043
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.06 | 602 | 1059 | 1461 | 1923
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.065 | 560 | 991 | 1373 | 1814
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.07 | 523 | 930 | 1294 | 1715
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.03 | 1024 | 1686 | 2236 | 2842
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.035 | 923 | 1544 | 2065 | 2644
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.04 | 837 | 1419 | 1913 | 2466
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.045 | 764 | 1310 | 1778 | 2306
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.05 | 700 | 1213 | 1657 | 2161
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.055 | 645 | 1128 | 1549 | 2030
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.06 | 598 | 1052 | 1452 | 1911
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.065 | 556 | 984 | 1364 | 1803
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00234 | 0.00195 | 0.00399 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82813 | 11.8637 | 135.936 | 0.07 | 519 | 923 | 1285 | 1704
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.03 | 1017 | 1675 | 2221 | 2824
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.035 | 916 | 1533 | 2051 | 2627
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.04 | 831 | 1409 | 1900 | 2450
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.045 | 757 | 1300 | 1765 | 2290
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.05 | 694 | 1204 | 1645 | 2145
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.055 | 640 | 1119 | 1537 | 2015
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.06 | 592 | 1043 | 1440 | 1896
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.065 | 551 | 976 | 1353 | 1789
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00232 | 0.00193 | 0.00394 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.8358 | 11.9185 | 135.936 | 0.07 | 514 | 915 | 1274 | 1690

## 25%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.03 | 3222 | 10740 | 13368 | 14290
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.035 | 3007 | 9314 | 11458 | 12249
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.04 | 2813 | 8231 | 10026 | 10718
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.045 | 2637 | 7378 | 8912 | 9527
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.05 | 2478 | 6688 | 8021 | 8574
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.055 | 2332 | 6116 | 7292 | 7795
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.06 | 2200 | 5635 | 6684 | 7145
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.065 | 2079 | 5225 | 6170 | 6595
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00303 | 0.00201 | 0.00255 | 0.00251 | 0.00339 | 0.00339 | 0.00201 | 0.00201 | 0.00201 | 0.73534 | 6.6659 | 92.736 | 0.07 | 1969 | 4870 | 5729 | 6124
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.03 | 2847 | 7231 | 11176 | 12854
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.035 | 2643 | 6419 | 9649 | 11018
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.04 | 2460 | 5782 | 8494 | 9641
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.045 | 2295 | 5266 | 7590 | 8569
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.05 | 2147 | 4837 | 6861 | 7712
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.055 | 2013 | 4472 | 6262 | 7011
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.06 | 1892 | 4158 | 5759 | 6427
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.065 | 1783 | 3885 | 5330 | 5933
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.003 | 0.00201 | 0.00253 | 0.00251 | 0.00331 | 0.00331 | 0.00201 | 0.00201 | 0.00201 | 0.73511 | 7.3664 | 92.736 | 0.07 | 1683 | 3644 | 4962 | 5509
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.03 | 2847 | 7231 | 11176 | 12854
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.035 | 2643 | 6419 | 9649 | 11018
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.04 | 2460 | 5782 | 8494 | 9641
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.045 | 2295 | 5266 | 7590 | 8569
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.05 | 2147 | 4837 | 6861 | 7712
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.055 | 2013 | 4472 | 6262 | 7011
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.06 | 1892 | 4158 | 5759 | 6427
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.065 | 1783 | 3885 | 5330 | 5933
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00297 | 0.00201 | 0.0025 | 0.00251 | 0.00324 | 0.00324 | 0.00201 | 0.00201 | 0.00201 | 0.73505 | 7.3661 | 92.736 | 0.07 | 1683 | 3644 | 4962 | 5509
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.03 | 2847 | 7231 | 11176 | 12854
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.035 | 2643 | 6419 | 9649 | 11018
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.04 | 2460 | 5782 | 8494 | 9641
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.045 | 2295 | 5266 | 7590 | 8569
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.05 | 2147 | 4837 | 6861 | 7712
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.055 | 2013 | 4472 | 6262 | 7011
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.06 | 1892 | 4158 | 5759 | 6427
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.065 | 1783 | 3885 | 5330 | 5933
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00295 | 0.00201 | 0.00247 | 0.00251 | 0.00315 | 0.00315 | 0.00201 | 0.00201 | 0.00201 | 0.73494 | 7.3656 | 92.736 | 0.07 | 1683 | 3644 | 4962 | 5509
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.03 | 2847 | 7231 | 11176 | 12854
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.035 | 2643 | 6419 | 9649 | 11018
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.04 | 2460 | 5782 | 8494 | 9641
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.045 | 2295 | 5266 | 7590 | 8569
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.05 | 2147 | 4837 | 6861 | 7712
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.055 | 2013 | 4472 | 6262 | 7011
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.06 | 1892 | 4158 | 5759 | 6427
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.065 | 1783 | 3885 | 5330 | 5933
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00292 | 0.00201 | 0.00244 | 0.00251 | 0.00306 | 0.00306 | 0.00201 | 0.00201 | 0.00201 | 0.73487 | 7.3652 | 92.736 | 0.07 | 1683 | 3644 | 4962 | 5509
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.03 | 2706 | 7360 | 10894 | 12178
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.035 | 2515 | 6494 | 9378 | 10439
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.04 | 2343 | 5820 | 8236 | 9134
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.045 | 2188 | 5279 | 7343 | 8119
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.05 | 2048 | 4832 | 6627 | 7307
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.055 | 1922 | 4455 | 6037 | 6643
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.06 | 1808 | 4133 | 5545 | 6089
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.065 | 1704 | 3854 | 5127 | 5621
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00266 | 0.00199 | 0.00223 | 0.00249 | 0.00298 | 0.00298 | 0.00199 | 0.00199 | 0.00199 | 0.73422 | 7.2349 | 99.936 | 0.07 | 1610 | 3609 | 4769 | 5219
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.03 | 2381 | 3778 | 8016 | 10886
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.035 | 2199 | 3539 | 7044 | 9331
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.04 | 2038 | 3321 | 6294 | 8164
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.045 | 1894 | 3123 | 5693 | 7257
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.05 | 1766 | 2942 | 5200 | 6531
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.055 | 1650 | 2777 | 4787 | 5938
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.06 | 1547 | 2625 | 4436 | 5443
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.065 | 1453 | 2486 | 4132 | 5024
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00263 | 0.00199 | 0.00221 | 0.00249 | 0.00289 | 0.00289 | 0.00199 | 0.00199 | 0.00199 | 0.73421 | 7.9964 | 99.936 | 0.07 | 1369 | 2359 | 3866 | 4665
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.03 | 2381 | 3778 | 8016 | 10886
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.035 | 2199 | 3539 | 7044 | 9331
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.04 | 2038 | 3321 | 6294 | 8164
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.045 | 1894 | 3123 | 5693 | 7257
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.05 | 1766 | 2942 | 5200 | 6531
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.055 | 1650 | 2777 | 4787 | 5938
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.06 | 1547 | 2625 | 4436 | 5443
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.065 | 1453 | 2486 | 4132 | 5024
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00261 | 0.00199 | 0.00219 | 0.00249 | 0.00282 | 0.00282 | 0.00199 | 0.00199 | 0.00199 | 0.73442 | 7.9976 | 99.936 | 0.07 | 1369 | 2359 | 3866 | 4665
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.03 | 2381 | 3778 | 8016 | 10886
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.035 | 2199 | 3539 | 7044 | 9331
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.04 | 2038 | 3321 | 6294 | 8164
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.045 | 1894 | 3123 | 5693 | 7257
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.05 | 1766 | 2942 | 5200 | 6531
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.055 | 1650 | 2777 | 4787 | 5938
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.06 | 1547 | 2625 | 4436 | 5443
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.065 | 1453 | 2486 | 4132 | 5024
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00258 | 0.00199 | 0.00216 | 0.00249 | 0.00276 | 0.00276 | 0.00199 | 0.00199 | 0.00199 | 0.73452 | 7.9981 | 99.936 | 0.07 | 1369 | 2359 | 3866 | 4665
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.03 | 2381 | 3778 | 8016 | 10886
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.035 | 2199 | 3539 | 7044 | 9331
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.04 | 2038 | 3321 | 6294 | 8164
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.045 | 1894 | 3123 | 5693 | 7257
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.05 | 1766 | 2942 | 5200 | 6531
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.055 | 1650 | 2777 | 4787 | 5938
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.06 | 1547 | 2625 | 4436 | 5443
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.065 | 1453 | 2486 | 4132 | 5024
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00255 | 0.00199 | 0.00215 | 0.00249 | 0.00269 | 0.00269 | 0.00199 | 0.00199 | 0.00199 | 0.73477 | 7.9995 | 99.936 | 0.07 | 1369 | 2359 | 3866 | 4665
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.03 | 2290 | 4349 | 8140 | 10434
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.035 | 2119 | 3981 | 7108 | 8944
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.04 | 1966 | 3673 | 6317 | 7826
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.045 | 1829 | 3409 | 5690 | 6956
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.05 | 1707 | 3179 | 5179 | 6260
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.055 | 1597 | 2976 | 4753 | 5691
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.06 | 1498 | 2796 | 4393 | 5217
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.065 | 1408 | 2634 | 4083 | 4816
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00236 | 0.00198 | 0.00198 | 0.00247 | 0.00264 | 0.00264 | 0.00198 | 0.00198 | 0.00198 | 0.73504 | 7.8135 | 107.136 | 0.07 | 1327 | 2488 | 3814 | 4472
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.03 | 2009 | 3210 | 5245 | 8323
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.035 | 1848 | 2995 | 4761 | 7250
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.04 | 1705 | 2800 | 4364 | 6431
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.045 | 1579 | 2623 | 4031 | 5784
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.05 | 1467 | 2463 | 3745 | 5257
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.055 | 1367 | 2318 | 3496 | 4821
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.06 | 1278 | 2185 | 3276 | 4451
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.065 | 1198 | 2064 | 3081 | 4133
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00234 | 0.00198 | 0.00198 | 0.00247 | 0.00258 | 0.00258 | 0.00198 | 0.00198 | 0.00198 | 0.73551 | 8.6387 | 107.136 | 0.07 | 1126 | 1954 | 2906 | 3859
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.03 | 2009 | 3210 | 5245 | 8323
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.035 | 1848 | 2995 | 4761 | 7250
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.04 | 1705 | 2800 | 4364 | 6431
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.045 | 1579 | 2623 | 4031 | 5784
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.05 | 1467 | 2463 | 3745 | 5257
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.055 | 1367 | 2318 | 3496 | 4821
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.06 | 1278 | 2185 | 3276 | 4451
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.065 | 1198 | 2064 | 3081 | 4133
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00231 | 0.00198 | 0.00198 | 0.00247 | 0.0025 | 0.0025 | 0.00198 | 0.00198 | 0.00198 | 0.73605 | 8.6419 | 107.136 | 0.07 | 1126 | 1954 | 2906 | 3859
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.03 | 2006 | 3206 | 5210 | 8295
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.035 | 1845 | 2990 | 4733 | 7227
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.04 | 1702 | 2796 | 4341 | 6413
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.045 | 1576 | 2619 | 4011 | 5768
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.05 | 1464 | 2459 | 3728 | 5244
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.055 | 1365 | 2314 | 3481 | 4809
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.06 | 1275 | 2182 | 3263 | 4441
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.065 | 1196 | 2061 | 3069 | 4125
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00229 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.7369 | 8.6469 | 107.136 | 0.07 | 1124 | 1951 | 2896 | 3851
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.03 | 2006 | 3206 | 5210 | 8295
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.035 | 1845 | 2990 | 4733 | 7227
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.04 | 1702 | 2796 | 4341 | 6413
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.045 | 1576 | 2619 | 4011 | 5768
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.05 | 1464 | 2459 | 3728 | 5244
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.055 | 1365 | 2314 | 3481 | 4809
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.06 | 1275 | 2182 | 3263 | 4441
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.065 | 1196 | 2061 | 3069 | 4125
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00227 | 0.00198 | 0.00198 | 0.00247 | 0.00247 | 0.00247 | 0.00198 | 0.00198 | 0.00198 | 0.73805 | 8.6536 | 107.136 | 0.07 | 1124 | 1951 | 2896 | 3851
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.03 | 1951 | 3109 | 5667 | 8415
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.035 | 1797 | 2904 | 5070 | 7283
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.04 | 1660 | 2719 | 4597 | 6425
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.045 | 1539 | 2551 | 4208 | 5752
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.05 | 1432 | 2398 | 3881 | 5208
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.055 | 1336 | 2259 | 3603 | 4759
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.06 | 1250 | 2132 | 3360 | 4381
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.065 | 1172 | 2016 | 3147 | 4059
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00211 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.73965 | 8.4144 | 114.336 | 0.07 | 1103 | 1909 | 2959 | 3782
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.03 | 1705 | 2743 | 3590 | 6003
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.035 | 1561 | 2548 | 3362 | 5368
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.04 | 1434 | 2373 | 3154 | 4865
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.045 | 1323 | 2216 | 2965 | 4453
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.05 | 1225 | 2074 | 2792 | 4108
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.055 | 1139 | 1945 | 2635 | 3812
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.06 | 1062 | 1829 | 2490 | 3556
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.065 | 993 | 1724 | 2358 | 3331
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00209 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74126 | 9.3102 | 114.336 | 0.07 | 932 | 1628 | 2237 | 3133
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.03 | 1703 | 2739 | 3586 | 5976
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.035 | 1558 | 2544 | 3357 | 5347
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.04 | 1432 | 2369 | 3150 | 4848
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.045 | 1321 | 2212 | 2961 | 4439
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.05 | 1223 | 2070 | 2788 | 4095
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.055 | 1137 | 1942 | 2631 | 3801
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.06 | 1060 | 1826 | 2487 | 3547
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.065 | 992 | 1721 | 2354 | 3323
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.00208 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74329 | 9.323 | 114.336 | 0.07 | 930 | 1626 | 2233 | 3126
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.03 | 1698 | 2732 | 3577 | 5923
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.035 | 1554 | 2537 | 3348 | 5304
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.04 | 1428 | 2363 | 3141 | 4813
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.045 | 1317 | 2205 | 2952 | 4410
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.05 | 1219 | 2064 | 2780 | 4071
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.055 | 1133 | 1936 | 2623 | 3780
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.06 | 1056 | 1820 | 2479 | 3528
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.065 | 988 | 1715 | 2347 | 3307
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00205 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74567 | 9.3379 | 114.336 | 0.07 | 927 | 1620 | 2226 | 3111
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.03 | 1693 | 2724 | 3567 | 5869
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.035 | 1549 | 2530 | 3339 | 5262
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.04 | 1423 | 2356 | 3132 | 4778
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.045 | 1313 | 2199 | 2944 | 4381
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.05 | 1215 | 2058 | 2772 | 4046
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.055 | 1129 | 1930 | 2615 | 3759
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.06 | 1053 | 1814 | 2471 | 3510
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.065 | 985 | 1710 | 2339 | 3291
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00203 | 0.00196 | 0.00196 | 0.00245 | 0.00245 | 0.00245 | 0.00196 | 0.00196 | 0.00196 | 0.74885 | 9.3578 | 114.336 | 0.07 | 924 | 1614 | 2219 | 3097
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.03 | 1661 | 2666 | 3485 | 6252
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.035 | 1523 | 2480 | 3268 | 5530
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.04 | 1402 | 2313 | 3070 | 4968
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.045 | 1295 | 2162 | 2889 | 4515
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.05 | 1200 | 2026 | 2724 | 4140
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.055 | 1117 | 1902 | 2573 | 3824
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.06 | 1042 | 1791 | 2434 | 3552
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.065 | 975 | 1689 | 2307 | 3317
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75322 | 9.0731 | 121.536 | 0.07 | 916 | 1596 | 2190 | 3109
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.03 | 1444 | 2340 | 3075 | 3880
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.035 | 1315 | 2164 | 2867 | 3642
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.04 | 1204 | 2007 | 2679 | 3425
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.045 | 1106 | 1867 | 2510 | 3227
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.05 | 1021 | 1741 | 2356 | 3046
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.055 | 946 | 1629 | 2216 | 2879
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.06 | 880 | 1527 | 2089 | 2726
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.065 | 822 | 1436 | 1973 | 2586
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.75795 | 10.0595 | 121.536 | 0.07 | 770 | 1353 | 1867 | 2456
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.03 | 1436 | 2328 | 3060 | 3862
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.035 | 1308 | 2152 | 2852 | 3624
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.04 | 1197 | 1996 | 2665 | 3408
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.045 | 1100 | 1856 | 2496 | 3210
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.05 | 1015 | 1731 | 2343 | 3029
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.055 | 940 | 1619 | 2203 | 2863
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.06 | 875 | 1518 | 2077 | 2711
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.065 | 816 | 1427 | 1961 | 2571
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.76474 | 10.1045 | 121.536 | 0.07 | 764 | 1345 | 1856 | 2442
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.03 | 1422 | 2307 | 3034 | 3830
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.035 | 1295 | 2132 | 2827 | 3594
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.04 | 1184 | 1977 | 2641 | 3378
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.045 | 1088 | 1838 | 2472 | 3181
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.05 | 1004 | 1713 | 2320 | 3000
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.055 | 930 | 1602 | 2181 | 2835
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.06 | 865 | 1502 | 2055 | 2684
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.065 | 807 | 1411 | 1940 | 2544
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.77393 | 10.1651 | 121.536 | 0.07 | 756 | 1330 | 1836 | 2416
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.03 | 1403 | 2278 | 2997 | 3786
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.035 | 1277 | 2104 | 2792 | 3550
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.04 | 1167 | 1950 | 2606 | 3336
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.045 | 1072 | 1812 | 2439 | 3140
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.05 | 988 | 1689 | 2287 | 2960
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.055 | 915 | 1578 | 2150 | 2796
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.06 | 851 | 1479 | 2025 | 2646
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.065 | 794 | 1389 | 1911 | 2508
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00244 | 0.00244 | 0.00195 | 0.00195 | 0.00195 | 0.79024 | 10.2716 | 121.536 | 0.07 | 743 | 1309 | 1808 | 2381
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.03 | 1401 | 2266 | 2975 | 4022
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.035 | 1278 | 2098 | 2777 | 3729
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.04 | 1171 | 1948 | 2598 | 3474
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.045 | 1077 | 1814 | 2436 | 3250
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.05 | 995 | 1693 | 2288 | 3051
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.055 | 923 | 1585 | 2154 | 2872
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.06 | 859 | 1488 | 2032 | 2710
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.065 | 802 | 1399 | 1921 | 2564
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.78605 | 9.8631 | 128.736 | 0.07 | 752 | 1319 | 1819 | 2430
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.03 | 1204 | 1967 | 2598 | 3291
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.035 | 1090 | 1810 | 2410 | 3075
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.04 | 993 | 1671 | 2242 | 2879
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.045 | 909 | 1547 | 2091 | 2701
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.05 | 836 | 1438 | 1956 | 2540
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.055 | 772 | 1340 | 1833 | 2393
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.06 | 716 | 1253 | 1722 | 2258
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.065 | 667 | 1175 | 1622 | 2136
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80019 | 10.9989 | 128.736 | 0.07 | 624 | 1104 | 1531 | 2023
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.03 | 1201 | 1963 | 2592 | 3284
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.035 | 1087 | 1805 | 2404 | 3068
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.04 | 990 | 1666 | 2237 | 2872
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.045 | 906 | 1543 | 2086 | 2695
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.05 | 833 | 1434 | 1950 | 2533
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.055 | 770 | 1336 | 1828 | 2386
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.06 | 714 | 1249 | 1718 | 2252
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.065 | 665 | 1171 | 1617 | 2130
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80298 | 11.0181 | 128.736 | 0.07 | 622 | 1101 | 1527 | 2018
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.03 | 1199 | 1960 | 2589 | 3280
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.035 | 1086 | 1803 | 2402 | 3064
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.04 | 989 | 1664 | 2234 | 2869
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.045 | 905 | 1541 | 2083 | 2691
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.05 | 832 | 1432 | 1948 | 2530
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.055 | 769 | 1334 | 1826 | 2383
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.06 | 713 | 1247 | 1715 | 2249
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.065 | 664 | 1170 | 1615 | 2127
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80486 | 11.031 | 128.736 | 0.07 | 621 | 1099 | 1524 | 2015
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.03 | 1196 | 1956 | 2583 | 3273
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.035 | 1083 | 1799 | 2396 | 3057
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.04 | 986 | 1660 | 2228 | 2862
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.045 | 902 | 1537 | 2078 | 2685
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.05 | 830 | 1428 | 1943 | 2524
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.055 | 766 | 1331 | 1821 | 2377
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.06 | 711 | 1244 | 1710 | 2243
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.065 | 662 | 1166 | 1611 | 2121
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00194 | 0.00194 | 0.00194 | 0.00243 | 0.00243 | 0.00243 | 0.00194 | 0.00194 | 0.00194 | 0.80696 | 11.0454 | 128.736 | 0.07 | 619 | 1096 | 1520 | 2009
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.03 | 1191 | 1941 | 2559 | 3237
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.035 | 1081 | 1789 | 2378 | 3030
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.04 | 986 | 1654 | 2216 | 2841
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.045 | 904 | 1534 | 2070 | 2670
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.05 | 833 | 1428 | 1938 | 2513
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.055 | 770 | 1332 | 1819 | 2371
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.06 | 715 | 1247 | 1711 | 2240
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.065 | 666 | 1170 | 1613 | 2121
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.81699 | 10.6614 | 135.936 | 0.07 | 623 | 1101 | 1524 | 2011
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.03 | 1029 | 1694 | 2245 | 2853
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.035 | 928 | 1551 | 2074 | 2656
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.04 | 842 | 1426 | 1923 | 2478
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.045 | 768 | 1316 | 1787 | 2317
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.05 | 704 | 1219 | 1666 | 2172
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.055 | 649 | 1134 | 1557 | 2040
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.06 | 601 | 1057 | 1459 | 1921
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.065 | 559 | 989 | 1371 | 1812
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82141 | 11.8155 | 135.936 | 0.07 | 522 | 928 | 1292 | 1713
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.03 | 1025 | 1688 | 2238 | 2845
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.035 | 924 | 1546 | 2067 | 2647
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.04 | 838 | 1421 | 1916 | 2469
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.045 | 765 | 1311 | 1780 | 2309
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.05 | 701 | 1215 | 1659 | 2164
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.055 | 646 | 1129 | 1551 | 2032
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.06 | 598 | 1053 | 1454 | 1913
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.065 | 557 | 985 | 1366 | 1805
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.82653 | 11.8522 | 135.936 | 0.07 | 520 | 924 | 1286 | 1706
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.03 | 1019 | 1679 | 2226 | 2830
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.035 | 918 | 1537 | 2056 | 2633
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.04 | 833 | 1412 | 1904 | 2455
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.045 | 760 | 1303 | 1770 | 2295
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.05 | 696 | 1207 | 1649 | 2151
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.055 | 642 | 1122 | 1541 | 2020
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.06 | 594 | 1046 | 1444 | 1901
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.065 | 552 | 978 | 1357 | 1793
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.83334 | 11.901 | 135.936 | 0.07 | 516 | 918 | 1278 | 1695
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.03 | 1012 | 1667 | 2212 | 2812
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.035 | 911 | 1526 | 2042 | 2615
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.04 | 826 | 1402 | 1891 | 2439
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.045 | 753 | 1293 | 1757 | 2279
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.05 | 691 | 1197 | 1637 | 2135
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.055 | 636 | 1113 | 1529 | 2005
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.06 | 589 | 1037 | 1433 | 1887
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.065 | 548 | 970 | 1346 | 1779
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00241 | 0.00241 | 0.00193 | 0.00193 | 0.00193 | 0.84104 | 11.9559 | 135.936 | 0.07 | 511 | 910 | 1267 | 1681

## 50%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.03 | 3204 | 10590 | 13302 | 14224
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.035 | 2990 | 9190 | 11402 | 12192
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.04 | 2796 | 8126 | 9977 | 10668
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.045 | 2621 | 7287 | 8868 | 9483
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.05 | 2462 | 6608 | 7981 | 8534
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.055 | 2317 | 6046 | 7256 | 7758
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.06 | 2185 | 5572 | 6651 | 7112
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.065 | 2065 | 5167 | 6139 | 6565
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00303 | 0.00201 | 0.00255 | 0.00302 | 0.00407 | 0.00407 | 0.00201 | 0.00201 | 0.00201 | 0.74243 | 6.6979 | 92.736 | 0.07 | 1955 | 4817 | 5701 | 6096
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.03 | 2833 | 7080 | 11056 | 12797
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.035 | 2629 | 6295 | 9551 | 10969
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.04 | 2446 | 5677 | 8413 | 9598
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.045 | 2282 | 5176 | 7521 | 8532
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.05 | 2134 | 4757 | 6802 | 7678
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.055 | 2001 | 4401 | 6209 | 6980
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.06 | 1880 | 4095 | 5712 | 6399
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.065 | 1771 | 3827 | 5288 | 5906
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.003 | 0.00201 | 0.00253 | 0.00302 | 0.00398 | 0.00398 | 0.00201 | 0.00201 | 0.00201 | 0.74218 | 7.4017 | 92.736 | 0.07 | 1672 | 3592 | 4924 | 5485
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.03 | 2833 | 7080 | 11056 | 12797
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.035 | 2629 | 6295 | 9551 | 10969
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.04 | 2446 | 5677 | 8413 | 9598
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.045 | 2282 | 5176 | 7521 | 8532
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.05 | 2134 | 4757 | 6802 | 7678
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.055 | 2001 | 4401 | 6209 | 6980
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.06 | 1880 | 4095 | 5712 | 6399
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.065 | 1771 | 3827 | 5288 | 5906
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00297 | 0.00201 | 0.0025 | 0.00302 | 0.00388 | 0.00388 | 0.00201 | 0.00201 | 0.00201 | 0.7421 | 7.4013 | 92.736 | 0.07 | 1672 | 3592 | 4924 | 5485
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.03 | 2833 | 7080 | 11056 | 12797
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.035 | 2629 | 6295 | 9551 | 10969
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.04 | 2446 | 5677 | 8413 | 9598
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.045 | 2282 | 5176 | 7521 | 8532
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.05 | 2134 | 4757 | 6802 | 7678
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.055 | 2001 | 4401 | 6209 | 6980
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.06 | 1880 | 4095 | 5712 | 6399
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.065 | 1771 | 3827 | 5288 | 5906
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00295 | 0.00201 | 0.00247 | 0.00302 | 0.00378 | 0.00378 | 0.00201 | 0.00201 | 0.00201 | 0.74197 | 7.4007 | 92.736 | 0.07 | 1672 | 3592 | 4924 | 5485
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.03 | 2833 | 7080 | 11056 | 12797
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.035 | 2629 | 6295 | 9551 | 10969
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.04 | 2446 | 5677 | 8413 | 9598
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.045 | 2282 | 5176 | 7521 | 8532
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.05 | 2134 | 4757 | 6802 | 7678
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.055 | 2001 | 4401 | 6209 | 6980
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.06 | 1880 | 4095 | 5712 | 6399
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.065 | 1771 | 3827 | 5288 | 5906
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00292 | 0.00201 | 0.00244 | 0.00302 | 0.00368 | 0.00368 | 0.00201 | 0.00201 | 0.00201 | 0.74188 | 7.4002 | 92.736 | 0.07 | 1672 | 3592 | 4924 | 5485
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.03 | 2688 | 7174 | 10745 | 12106
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.035 | 2497 | 6340 | 9257 | 10377
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.04 | 2325 | 5690 | 8135 | 9079
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.045 | 2171 | 5167 | 7257 | 8071
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.05 | 2032 | 4733 | 6553 | 7264
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.055 | 1907 | 4368 | 5973 | 6603
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.06 | 1793 | 4054 | 5488 | 6053
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.065 | 1690 | 3782 | 5076 | 5587
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00266 | 0.00199 | 0.00223 | 0.00298 | 0.00357 | 0.00357 | 0.00199 | 0.00199 | 0.00199 | 0.74108 | 7.2686 | 99.936 | 0.07 | 1596 | 3545 | 4722 | 5188
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.03 | 2369 | 3761 | 7904 | 10794
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.035 | 2188 | 3522 | 6953 | 9258
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.04 | 2027 | 3305 | 6218 | 8105
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.045 | 1884 | 3107 | 5629 | 7207
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.05 | 1756 | 2927 | 5145 | 6489
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.055 | 1641 | 2762 | 4738 | 5902
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.06 | 1538 | 2611 | 4392 | 5412
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.065 | 1445 | 2472 | 4093 | 4996
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00263 | 0.00199 | 0.00221 | 0.00298 | 0.00347 | 0.00347 | 0.00199 | 0.00199 | 0.00199 | 0.74106 | 8.0336 | 99.936 | 0.07 | 1361 | 2345 | 3831 | 4640
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.03 | 2369 | 3761 | 7904 | 10794
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.035 | 2188 | 3522 | 6953 | 9258
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.04 | 2027 | 3305 | 6218 | 8105
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.045 | 1884 | 3107 | 5629 | 7207
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.05 | 1756 | 2927 | 5145 | 6489
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.055 | 1641 | 2762 | 4738 | 5902
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.06 | 1538 | 2611 | 4392 | 5412
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.065 | 1445 | 2472 | 4093 | 4996
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00261 | 0.00199 | 0.00219 | 0.00298 | 0.00339 | 0.00339 | 0.00199 | 0.00199 | 0.00199 | 0.74127 | 8.0348 | 99.936 | 0.07 | 1361 | 2345 | 3831 | 4640
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.03 | 2366 | 3756 | 7866 | 10763
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.035 | 2185 | 3517 | 6923 | 9234
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.04 | 2024 | 3300 | 6193 | 8085
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.045 | 1881 | 3102 | 5607 | 7191
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.05 | 1753 | 2922 | 5126 | 6475
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.055 | 1638 | 2757 | 4722 | 5890
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.06 | 1535 | 2606 | 4378 | 5401
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.065 | 1442 | 2468 | 4080 | 4987
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00258 | 0.00199 | 0.00216 | 0.00298 | 0.00332 | 0.00332 | 0.00199 | 0.00199 | 0.00199 | 0.74137 | 8.0353 | 99.936 | 0.07 | 1358 | 2341 | 3820 | 4632
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.03 | 2366 | 3756 | 7866 | 10763
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.035 | 2185 | 3517 | 6923 | 9234
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.04 | 2024 | 3300 | 6193 | 8085
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.045 | 1881 | 3102 | 5607 | 7191
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.05 | 1753 | 2922 | 5126 | 6475
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.055 | 1638 | 2757 | 4722 | 5890
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.06 | 1535 | 2606 | 4378 | 5401
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.065 | 1442 | 2468 | 4080 | 4987
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00255 | 0.00199 | 0.00215 | 0.00298 | 0.00323 | 0.00323 | 0.00199 | 0.00199 | 0.00199 | 0.74162 | 8.0367 | 99.936 | 0.07 | 1358 | 2341 | 3820 | 4632
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.03 | 2275 | 4175 | 8000 | 10374
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.035 | 2104 | 3838 | 6995 | 8892
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.04 | 1952 | 3552 | 6223 | 7781
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.045 | 1816 | 3305 | 5610 | 6916
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.05 | 1694 | 3087 | 5110 | 6225
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.055 | 1584 | 2895 | 4693 | 5659
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.06 | 1486 | 2723 | 4339 | 5187
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.065 | 1397 | 2567 | 4034 | 4788
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00236 | 0.00198 | 0.00198 | 0.00297 | 0.00316 | 0.00316 | 0.00198 | 0.00198 | 0.00198 | 0.74179 | 7.8493 | 107.136 | 0.07 | 1317 | 2427 | 3770 | 4446
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.03 | 1997 | 3192 | 5106 | 8209
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.035 | 1836 | 2977 | 4648 | 7159
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.04 | 1694 | 2783 | 4270 | 6357
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.045 | 1568 | 2607 | 3951 | 5722
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.05 | 1457 | 2447 | 3676 | 5205
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.055 | 1357 | 2302 | 3436 | 4776
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.06 | 1268 | 2170 | 3222 | 4412
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.065 | 1189 | 2050 | 3033 | 4099
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00234 | 0.00198 | 0.00198 | 0.00297 | 0.00309 | 0.00309 | 0.00198 | 0.00198 | 0.00198 | 0.74226 | 8.6783 | 107.136 | 0.07 | 1117 | 1940 | 2863 | 3828
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.03 | 1997 | 3192 | 5106 | 8209
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.035 | 1836 | 2977 | 4648 | 7159
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.04 | 1694 | 2783 | 4270 | 6357
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.045 | 1568 | 2607 | 3951 | 5722
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.05 | 1457 | 2447 | 3676 | 5205
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.055 | 1357 | 2302 | 3436 | 4776
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.06 | 1268 | 2170 | 3222 | 4412
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.065 | 1189 | 2050 | 3033 | 4099
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00231 | 0.00198 | 0.00198 | 0.00297 | 0.003 | 0.003 | 0.00198 | 0.00198 | 0.00198 | 0.74283 | 8.6816 | 107.136 | 0.07 | 1117 | 1940 | 2863 | 3828
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.03 | 1994 | 3188 | 5071 | 8180
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.035 | 1833 | 2973 | 4620 | 7137
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.04 | 1691 | 2778 | 4246 | 6339
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.045 | 1566 | 2603 | 3931 | 5707
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.05 | 1454 | 2443 | 3659 | 5192
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.055 | 1355 | 2298 | 3420 | 4764
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.06 | 1266 | 2167 | 3209 | 4402
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.065 | 1187 | 2046 | 3021 | 4090
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00229 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74371 | 8.6868 | 107.136 | 0.07 | 1115 | 1937 | 2852 | 3821
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.03 | 1994 | 3188 | 5071 | 8180
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.035 | 1833 | 2973 | 4620 | 7137
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.04 | 1691 | 2778 | 4246 | 6339
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.045 | 1566 | 2603 | 3931 | 5707
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.05 | 1454 | 2443 | 3659 | 5192
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.055 | 1355 | 2298 | 3420 | 4764
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.06 | 1266 | 2167 | 3209 | 4402
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.065 | 1187 | 2046 | 3021 | 4090
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00227 | 0.00198 | 0.00198 | 0.00297 | 0.00297 | 0.00297 | 0.00198 | 0.00198 | 0.00198 | 0.74492 | 8.6938 | 107.136 | 0.07 | 1115 | 1937 | 2852 | 3821
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.03 | 1939 | 3091 | 5536 | 8308
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.035 | 1785 | 2887 | 4964 | 7198
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.04 | 1649 | 2702 | 4508 | 6356
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.045 | 1529 | 2534 | 4133 | 5694
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.05 | 1422 | 2382 | 3816 | 5159
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.055 | 1326 | 2243 | 3546 | 4717
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.06 | 1240 | 2117 | 3310 | 4344
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.065 | 1163 | 2001 | 3102 | 4027
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00211 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74645 | 8.453 | 114.336 | 0.07 | 1094 | 1895 | 2918 | 3753
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.03 | 1695 | 2728 | 3572 | 5896
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.035 | 1551 | 2534 | 3344 | 5283
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.04 | 1425 | 2359 | 3137 | 4796
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.045 | 1315 | 2202 | 2948 | 4396
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.05 | 1217 | 2061 | 2776 | 4059
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.055 | 1131 | 1933 | 2619 | 3770
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.06 | 1055 | 1817 | 2475 | 3519
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.065 | 986 | 1713 | 2343 | 3299
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00209 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.74812 | 9.3532 | 114.336 | 0.07 | 925 | 1617 | 2222 | 3104
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.03 | 1690 | 2721 | 3563 | 5842
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.035 | 1547 | 2527 | 3335 | 5240
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.04 | 1421 | 2352 | 3128 | 4761
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.045 | 1311 | 2196 | 2939 | 4367
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.05 | 1213 | 2054 | 2768 | 4034
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.055 | 1127 | 1927 | 2611 | 3749
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.06 | 1051 | 1812 | 2467 | 3501
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.065 | 983 | 1707 | 2336 | 3283
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00208 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75023 | 9.3664 | 114.336 | 0.07 | 922 | 1612 | 2215 | 3090
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.03 | 1688 | 2717 | 3558 | 5816
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.035 | 1544 | 2523 | 3331 | 5219
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.04 | 1419 | 2349 | 3124 | 4744
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.045 | 1309 | 2192 | 2935 | 4352
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.05 | 1211 | 2051 | 2763 | 4022
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.055 | 1125 | 1924 | 2607 | 3738
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.06 | 1049 | 1809 | 2463 | 3492
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.065 | 981 | 1704 | 2332 | 3275
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00205 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75268 | 9.3817 | 114.336 | 0.07 | 920 | 1609 | 2211 | 3082
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.03 | 1683 | 2710 | 3549 | 5762
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.035 | 1540 | 2516 | 3322 | 5176
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.04 | 1414 | 2342 | 3115 | 4709
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.045 | 1304 | 2186 | 2927 | 4324
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.05 | 1207 | 2045 | 2755 | 3997
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.055 | 1122 | 1918 | 2599 | 3717
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.06 | 1045 | 1803 | 2456 | 3473
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.065 | 978 | 1698 | 2324 | 3258
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00203 | 0.00196 | 0.00196 | 0.00294 | 0.00294 | 0.00294 | 0.00196 | 0.00196 | 0.00196 | 0.75593 | 9.402 | 114.336 | 0.07 | 917 | 1604 | 2204 | 3068
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.03 | 1649 | 2647 | 3462 | 6126
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.035 | 1511 | 2462 | 3245 | 5430
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.04 | 1391 | 2296 | 3048 | 4887
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.045 | 1284 | 2145 | 2868 | 4447
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.05 | 1190 | 2010 | 2703 | 4083
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.055 | 1107 | 1887 | 2553 | 3774
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.06 | 1033 | 1776 | 2415 | 3509
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.065 | 967 | 1675 | 2288 | 3279
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76023 | 9.1152 | 121.536 | 0.07 | 908 | 1583 | 2171 | 3076
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.03 | 1434 | 2325 | 3056 | 3857
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.035 | 1306 | 2149 | 2849 | 3620
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.04 | 1195 | 1993 | 2662 | 3404
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.045 | 1098 | 1853 | 2493 | 3206
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.05 | 1013 | 1729 | 2339 | 3025
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.055 | 939 | 1616 | 2200 | 2859
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.06 | 873 | 1516 | 2073 | 2707
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.065 | 815 | 1425 | 1958 | 2567
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.76501 | 10.1063 | 121.536 | 0.07 | 763 | 1342 | 1853 | 2438
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.03 | 1426 | 2313 | 3041 | 3839
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.035 | 1298 | 2138 | 2834 | 3602
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.04 | 1188 | 1982 | 2648 | 3386
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.045 | 1091 | 1843 | 2479 | 3189
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.05 | 1007 | 1718 | 2326 | 3009
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.055 | 933 | 1607 | 2187 | 2843
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.06 | 867 | 1506 | 2061 | 2691
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.065 | 810 | 1416 | 1946 | 2552
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.77178 | 10.1509 | 121.536 | 0.07 | 758 | 1334 | 1841 | 2423
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.03 | 1415 | 2296 | 3019 | 3812
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.035 | 1288 | 2121 | 2813 | 3576
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.04 | 1177 | 1966 | 2627 | 3361
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.045 | 1081 | 1827 | 2459 | 3164
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.05 | 998 | 1703 | 2307 | 2984
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.055 | 924 | 1592 | 2169 | 2820
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.06 | 859 | 1493 | 2043 | 2668
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.065 | 802 | 1403 | 1929 | 2530
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.78071 | 10.2095 | 121.536 | 0.07 | 751 | 1321 | 1824 | 2402
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.03 | 1396 | 2267 | 2983 | 3768
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.035 | 1269 | 2093 | 2778 | 3533
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.04 | 1160 | 1939 | 2593 | 3319
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.045 | 1065 | 1802 | 2426 | 3123
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.05 | 982 | 1679 | 2275 | 2945
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.055 | 909 | 1569 | 2138 | 2781
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.06 | 845 | 1470 | 2013 | 2631
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.065 | 789 | 1381 | 1900 | 2493
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00292 | 0.00292 | 0.00195 | 0.00195 | 0.00195 | 0.79579 | 10.3076 | 121.536 | 0.07 | 738 | 1300 | 1797 | 2367
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.03 | 1393 | 2254 | 2960 | 3927
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.035 | 1271 | 2087 | 2763 | 3653
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.04 | 1164 | 1937 | 2584 | 3413
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.045 | 1070 | 1803 | 2422 | 3199
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.05 | 989 | 1683 | 2275 | 3008
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.055 | 917 | 1575 | 2142 | 2834
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.06 | 853 | 1478 | 2020 | 2677
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.065 | 797 | 1390 | 1909 | 2535
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.79268 | 9.9046 | 128.736 | 0.07 | 747 | 1311 | 1807 | 2404
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.03 | 1199 | 1960 | 2589 | 3280
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.035 | 1086 | 1803 | 2402 | 3064
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.04 | 989 | 1664 | 2234 | 2869
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.045 | 905 | 1541 | 2083 | 2691
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.05 | 832 | 1432 | 1948 | 2530
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.055 | 769 | 1334 | 1826 | 2383
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.06 | 713 | 1247 | 1715 | 2249
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.065 | 664 | 1170 | 1615 | 2127
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80531 | 11.0341 | 128.736 | 0.07 | 621 | 1099 | 1524 | 2015
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.03 | 1196 | 1956 | 2583 | 3273
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.035 | 1083 | 1799 | 2396 | 3057
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.04 | 986 | 1660 | 2228 | 2862
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.045 | 902 | 1537 | 2078 | 2685
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.05 | 830 | 1428 | 1943 | 2524
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.055 | 766 | 1331 | 1821 | 2377
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.06 | 711 | 1244 | 1710 | 2243
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.065 | 662 | 1166 | 1611 | 2121
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80789 | 11.0518 | 128.736 | 0.07 | 619 | 1096 | 1520 | 2009
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.03 | 1194 | 1953 | 2580 | 3269
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.035 | 1082 | 1796 | 2393 | 3054
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.04 | 985 | 1658 | 2226 | 2858
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.045 | 901 | 1535 | 2075 | 2681
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.05 | 829 | 1426 | 1940 | 2520
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.055 | 765 | 1329 | 1818 | 2374
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.06 | 710 | 1242 | 1708 | 2240
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.065 | 661 | 1164 | 1608 | 2118
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.80978 | 11.0646 | 128.736 | 0.07 | 618 | 1095 | 1518 | 2006
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.03 | 1191 | 1949 | 2574 | 3262
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.035 | 1079 | 1792 | 2387 | 3047
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.04 | 982 | 1653 | 2220 | 2852
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.045 | 898 | 1531 | 2070 | 2675
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.05 | 826 | 1422 | 1935 | 2514
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.055 | 763 | 1325 | 1813 | 2368
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.06 | 708 | 1239 | 1703 | 2234
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.065 | 659 | 1161 | 1604 | 2112
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00291 | 0.00291 | 0.00194 | 0.00194 | 0.00194 | 0.81188 | 11.079 | 128.736 | 0.07 | 616 | 1091 | 1513 | 2001
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.03 | 1187 | 1934 | 2550 | 3226
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.035 | 1077 | 1782 | 2370 | 3019
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.04 | 982 | 1648 | 2208 | 2831
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.045 | 900 | 1528 | 2062 | 2660
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.05 | 829 | 1422 | 1930 | 2504
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.055 | 766 | 1327 | 1812 | 2361
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.06 | 712 | 1241 | 1704 | 2231
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.065 | 663 | 1165 | 1606 | 2112
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82192 | 10.6935 | 135.936 | 0.07 | 620 | 1096 | 1517 | 2002
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.03 | 1025 | 1688 | 2238 | 2845
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.035 | 924 | 1546 | 2067 | 2647
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.04 | 838 | 1421 | 1916 | 2469
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.045 | 765 | 1311 | 1780 | 2309
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.05 | 701 | 1215 | 1659 | 2164
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.055 | 646 | 1129 | 1551 | 2032
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.06 | 598 | 1053 | 1454 | 1913
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.065 | 557 | 985 | 1366 | 1805
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.82635 | 11.851 | 135.936 | 0.07 | 520 | 924 | 1286 | 1706
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.03 | 1020 | 1680 | 2228 | 2833
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.035 | 920 | 1538 | 2058 | 2635
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.04 | 834 | 1414 | 1907 | 2458
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.045 | 761 | 1305 | 1772 | 2298
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.05 | 697 | 1208 | 1651 | 2153
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.055 | 643 | 1123 | 1543 | 2022
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.06 | 595 | 1047 | 1446 | 1904
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.065 | 553 | 980 | 1358 | 1795
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83147 | 11.8877 | 135.936 | 0.07 | 517 | 919 | 1279 | 1697
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.03 | 1014 | 1671 | 2216 | 2818
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.035 | 914 | 1529 | 2046 | 2621
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.04 | 828 | 1405 | 1896 | 2444
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.045 | 755 | 1297 | 1761 | 2284
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.05 | 693 | 1201 | 1641 | 2140
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.055 | 638 | 1116 | 1533 | 2010
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.06 | 591 | 1040 | 1436 | 1891
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.065 | 549 | 973 | 1349 | 1784
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.83829 | 11.9363 | 135.936 | 0.07 | 513 | 913 | 1271 | 1686
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.03 | 1008 | 1662 | 2204 | 2803
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.035 | 908 | 1520 | 2035 | 2607
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.04 | 823 | 1397 | 1884 | 2430
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.045 | 750 | 1288 | 1750 | 2271
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.05 | 688 | 1193 | 1631 | 2127
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.055 | 634 | 1108 | 1523 | 1997
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.06 | 587 | 1033 | 1427 | 1879
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.065 | 545 | 966 | 1340 | 1772
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.0029 | 0.0029 | 0.00193 | 0.00193 | 0.00193 | 0.846 | 11.9911 | 135.936 | 0.07 | 509 | 907 | 1262 | 1675

## 50%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.03 | 3187 | 10439 | 13237 | 14158
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.035 | 2973 | 9066 | 11346 | 12136
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.04 | 2780 | 8021 | 9927 | 10619
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.045 | 2605 | 7197 | 8824 | 9439
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.05 | 2446 | 6529 | 7942 | 8495
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.055 | 2302 | 5975 | 7220 | 7723
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.06 | 2171 | 5509 | 6618 | 7079
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.065 | 2051 | 5110 | 6109 | 6535
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00692 | 0.00573 | 0.01191 | 0.00455 | 0.00302 | 0.00383 | 0.00302 | 0.00407 | 0.00407 | 0.00302 | 0.00302 | 0.00302 | 0.7506 | 6.7347 | 92.736 | 0.07 | 1941 | 4764 | 5673 | 6068
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.03 | 2814 | 6880 | 10894 | 12722
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.035 | 2610 | 6130 | 9421 | 10905
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.04 | 2428 | 5538 | 8304 | 9542
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.045 | 2265 | 5055 | 7429 | 8481
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.05 | 2118 | 4652 | 6722 | 7633
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.055 | 1985 | 4307 | 6139 | 6939
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.06 | 1865 | 4011 | 5650 | 6361
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.065 | 1756 | 3751 | 5233 | 5872
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00683 | 0.00566 | 0.01177 | 0.0045 | 0.00302 | 0.0038 | 0.00302 | 0.00398 | 0.00398 | 0.00302 | 0.00302 | 0.00302 | 0.75033 | 7.4422 | 92.736 | 0.07 | 1658 | 3522 | 4874 | 5452
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.03 | 2814 | 6880 | 10894 | 12722
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.035 | 2610 | 6130 | 9421 | 10905
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.04 | 2428 | 5538 | 8304 | 9542
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.045 | 2265 | 5055 | 7429 | 8481
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.05 | 2118 | 4652 | 6722 | 7633
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.055 | 1985 | 4307 | 6139 | 6939
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.06 | 1865 | 4011 | 5650 | 6361
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.065 | 1756 | 3751 | 5233 | 5872
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00678 | 0.00561 | 0.01166 | 0.00445 | 0.00302 | 0.00375 | 0.00302 | 0.00388 | 0.00388 | 0.00302 | 0.00302 | 0.00302 | 0.75026 | 7.4419 | 92.736 | 0.07 | 1658 | 3522 | 4874 | 5452
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.03 | 2814 | 6880 | 10894 | 12722
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.035 | 2610 | 6130 | 9421 | 10905
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.04 | 2428 | 5538 | 8304 | 9542
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.045 | 2265 | 5055 | 7429 | 8481
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.05 | 2118 | 4652 | 6722 | 7633
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.055 | 1985 | 4307 | 6139 | 6939
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.06 | 1865 | 4011 | 5650 | 6361
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.065 | 1756 | 3751 | 5233 | 5872
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00671 | 0.00554 | 0.01153 | 0.00443 | 0.00302 | 0.0037 | 0.00302 | 0.00378 | 0.00378 | 0.00302 | 0.00302 | 0.00302 | 0.75014 | 7.4413 | 92.736 | 0.07 | 1658 | 3522 | 4874 | 5452
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.03 | 2814 | 6880 | 10894 | 12722
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.035 | 2610 | 6130 | 9421 | 10905
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.04 | 2428 | 5538 | 8304 | 9542
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.045 | 2265 | 5055 | 7429 | 8481
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.05 | 2118 | 4652 | 6722 | 7633
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.055 | 1985 | 4307 | 6139 | 6939
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.06 | 1865 | 4011 | 5650 | 6361
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.065 | 1756 | 3751 | 5233 | 5872
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00665 | 0.00549 | 0.01141 | 0.00438 | 0.00302 | 0.00366 | 0.00302 | 0.00368 | 0.00368 | 0.00302 | 0.00302 | 0.00302 | 0.75003 | 7.4408 | 92.736 | 0.07 | 1658 | 3522 | 4874 | 5452
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.03 | 2669 | 6988 | 10595 | 12034
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.035 | 2479 | 6187 | 9135 | 10315
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.04 | 2308 | 5560 | 8034 | 9026
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.045 | 2154 | 5055 | 7172 | 8023
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.05 | 2016 | 4635 | 6479 | 7221
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.055 | 1891 | 4281 | 5908 | 6564
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.06 | 1778 | 3976 | 5430 | 6017
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.065 | 1675 | 3711 | 5024 | 5554
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00603 | 0.005 | 0.01037 | 0.00399 | 0.00298 | 0.00335 | 0.00298 | 0.00357 | 0.00357 | 0.00298 | 0.00298 | 0.00298 | 0.74934 | 7.309 | 99.936 | 0.07 | 1582 | 3480 | 4675 | 5158
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.03 | 2351 | 3733 | 7717 | 10641
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.035 | 2170 | 3495 | 6802 | 9136
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.04 | 2010 | 3279 | 6092 | 8005
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.045 | 1867 | 3081 | 5522 | 7125
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.05 | 1740 | 2902 | 5052 | 6419
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.055 | 1625 | 2737 | 4657 | 5842
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.06 | 1523 | 2587 | 4320 | 5359
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.065 | 1430 | 2449 | 4028 | 4950
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00597 | 0.00495 | 0.01026 | 0.00394 | 0.00298 | 0.00332 | 0.00298 | 0.00347 | 0.00347 | 0.00298 | 0.00298 | 0.00298 | 0.74932 | 8.0783 | 99.936 | 0.07 | 1347 | 2323 | 3773 | 4599
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.03 | 2351 | 3733 | 7717 | 10641
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.035 | 2170 | 3495 | 6802 | 9136
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.04 | 2010 | 3279 | 6092 | 8005
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.045 | 1867 | 3081 | 5522 | 7125
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.05 | 1740 | 2902 | 5052 | 6419
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.055 | 1625 | 2737 | 4657 | 5842
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.06 | 1523 | 2587 | 4320 | 5359
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.065 | 1430 | 2449 | 4028 | 4950
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00593 | 0.0049 | 0.01016 | 0.00392 | 0.00298 | 0.00329 | 0.00298 | 0.00339 | 0.00339 | 0.00298 | 0.00298 | 0.00298 | 0.74958 | 8.0797 | 99.936 | 0.07 | 1347 | 2323 | 3773 | 4599
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.03 | 2351 | 3733 | 7717 | 10641
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.035 | 2170 | 3495 | 6802 | 9136
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.04 | 2010 | 3279 | 6092 | 8005
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.045 | 1867 | 3081 | 5522 | 7125
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.05 | 1740 | 2902 | 5052 | 6419
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.055 | 1625 | 2737 | 4657 | 5842
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.06 | 1523 | 2587 | 4320 | 5359
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.065 | 1430 | 2449 | 4028 | 4950
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00585 | 0.00486 | 0.01005 | 0.00387 | 0.00298 | 0.00324 | 0.00298 | 0.00332 | 0.00332 | 0.00298 | 0.00298 | 0.00298 | 0.74969 | 8.0803 | 99.936 | 0.07 | 1347 | 2323 | 3773 | 4599
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.03 | 2351 | 3733 | 7717 | 10641
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.035 | 2170 | 3495 | 6802 | 9136
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.04 | 2010 | 3279 | 6092 | 8005
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.045 | 1867 | 3081 | 5522 | 7125
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.05 | 1740 | 2902 | 5052 | 6419
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.055 | 1625 | 2737 | 4657 | 5842
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.06 | 1523 | 2587 | 4320 | 5359
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.065 | 1430 | 2449 | 4028 | 4950
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00581 | 0.0048 | 0.00994 | 0.00383 | 0.00298 | 0.00323 | 0.00298 | 0.00323 | 0.00323 | 0.00298 | 0.00298 | 0.00298 | 0.74996 | 8.0817 | 99.936 | 0.07 | 1347 | 2323 | 3773 | 4599
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.03 | 2261 | 4001 | 7861 | 10315
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.035 | 2090 | 3695 | 6882 | 8841
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.04 | 1938 | 3431 | 6129 | 7736
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.045 | 1803 | 3200 | 5530 | 6877
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.05 | 1681 | 2996 | 5041 | 6189
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.055 | 1572 | 2814 | 4632 | 5626
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.06 | 1474 | 2650 | 4285 | 5157
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.065 | 1386 | 2501 | 3986 | 4761
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00534 | 0.00444 | 0.00915 | 0.00354 | 0.00297 | 0.00297 | 0.00297 | 0.00316 | 0.00316 | 0.00297 | 0.00297 | 0.00297 | 0.75038 | 7.8946 | 107.136 | 0.07 | 1306 | 2367 | 3726 | 4421
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.03 | 1982 | 3170 | 4931 | 8066
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.035 | 1822 | 2955 | 4506 | 7046
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.04 | 1680 | 2762 | 4152 | 6265
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.045 | 1555 | 2586 | 3851 | 5645
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.05 | 1444 | 2427 | 3589 | 5140
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.055 | 1345 | 2283 | 3360 | 4720
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.06 | 1257 | 2152 | 3155 | 4363
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.065 | 1178 | 2032 | 2973 | 4056
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00528 | 0.00439 | 0.00906 | 0.00351 | 0.00297 | 0.00297 | 0.00297 | 0.00309 | 0.00309 | 0.00297 | 0.00297 | 0.00297 | 0.75092 | 8.7288 | 107.136 | 0.07 | 1107 | 1923 | 2808 | 3790
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.03 | 1982 | 3170 | 4931 | 8066
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.035 | 1822 | 2955 | 4506 | 7046
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.04 | 1680 | 2762 | 4152 | 6265
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.045 | 1555 | 2586 | 3851 | 5645
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.05 | 1444 | 2427 | 3589 | 5140
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.055 | 1345 | 2283 | 3360 | 4720
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.06 | 1257 | 2152 | 3155 | 4363
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.065 | 1178 | 2032 | 2973 | 4056
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00524 | 0.00435 | 0.00897 | 0.00347 | 0.00297 | 0.00297 | 0.00297 | 0.003 | 0.003 | 0.00297 | 0.00297 | 0.00297 | 0.75155 | 8.7324 | 107.136 | 0.07 | 1107 | 1923 | 2808 | 3790
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.03 | 1979 | 3166 | 4897 | 8037
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.035 | 1819 | 2951 | 4478 | 7023
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.04 | 1677 | 2757 | 4129 | 6246
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.045 | 1552 | 2582 | 3831 | 5630
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.05 | 1441 | 2423 | 3572 | 5127
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.055 | 1343 | 2279 | 3345 | 4708
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.06 | 1255 | 2148 | 3142 | 4353
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.065 | 1176 | 2028 | 2961 | 4047
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00517 | 0.0043 | 0.00888 | 0.00343 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.7525 | 8.738 | 107.136 | 0.07 | 1105 | 1919 | 2797 | 3782
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.03 | 1976 | 3161 | 4862 | 8009
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.035 | 1816 | 2947 | 4450 | 7000
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.04 | 1675 | 2753 | 4105 | 6228
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.045 | 1550 | 2578 | 3811 | 5614
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.05 | 1439 | 2419 | 3555 | 5114
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.055 | 1340 | 2275 | 3330 | 4697
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.06 | 1252 | 2144 | 3128 | 4343
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.065 | 1173 | 2025 | 2949 | 4038
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00513 | 0.00426 | 0.00879 | 0.00341 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.00297 | 0.75379 | 8.7454 | 107.136 | 0.07 | 1103 | 1916 | 2786 | 3774
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.03 | 1921 | 3064 | 5340 | 8147
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.035 | 1768 | 2861 | 4805 | 7070
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.04 | 1633 | 2677 | 4376 | 6252
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.045 | 1513 | 2510 | 4021 | 5607
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.05 | 1406 | 2358 | 3719 | 5086
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.055 | 1311 | 2220 | 3461 | 4653
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.06 | 1226 | 2094 | 3234 | 4289
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.065 | 1150 | 1980 | 3034 | 3978
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00479 | 0.00398 | 0.00819 | 0.00317 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75578 | 8.5057 | 114.336 | 0.07 | 1082 | 1875 | 2857 | 3710
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.03 | 1681 | 2706 | 3545 | 5735
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.035 | 1537 | 2512 | 3317 | 5155
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.04 | 1412 | 2339 | 3111 | 4692
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.045 | 1302 | 2182 | 2923 | 4309
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.05 | 1205 | 2042 | 2751 | 3985
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.055 | 1120 | 1915 | 2595 | 3707
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.06 | 1044 | 1800 | 2452 | 3464
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.065 | 976 | 1696 | 2321 | 3250
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00474 | 0.00394 | 0.00812 | 0.00314 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75756 | 9.4121 | 114.336 | 0.07 | 916 | 1601 | 2201 | 3061
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.03 | 1676 | 2699 | 3536 | 5682
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.035 | 1533 | 2506 | 3308 | 5113
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.04 | 1408 | 2332 | 3102 | 4657
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.045 | 1298 | 2176 | 2914 | 4280
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.05 | 1201 | 2035 | 2743 | 3961
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.055 | 1116 | 1909 | 2587 | 3686
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.06 | 1040 | 1794 | 2444 | 3446
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.065 | 973 | 1690 | 2313 | 3234
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00469 | 0.0039 | 0.00802 | 0.00312 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.75981 | 9.426 | 114.336 | 0.07 | 912 | 1595 | 2193 | 3046
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.03 | 1674 | 2696 | 3531 | 5655
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.035 | 1531 | 2502 | 3304 | 5091
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.04 | 1406 | 2329 | 3098 | 4640
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.045 | 1296 | 2173 | 2910 | 4266
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.05 | 1199 | 2032 | 2739 | 3949
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.055 | 1114 | 1906 | 2583 | 3675
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.06 | 1038 | 1791 | 2440 | 3437
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.065 | 971 | 1687 | 2310 | 3226
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00465 | 0.00387 | 0.00795 | 0.00308 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76237 | 9.4419 | 114.336 | 0.07 | 911 | 1593 | 2190 | 3039
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.03 | 1669 | 2688 | 3522 | 5601
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.035 | 1526 | 2495 | 3295 | 5049
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.04 | 1401 | 2322 | 3089 | 4605
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.045 | 1292 | 2166 | 2902 | 4237
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.05 | 1195 | 2026 | 2731 | 3924
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.055 | 1110 | 1900 | 2575 | 3654
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.06 | 1035 | 1785 | 2433 | 3418
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.065 | 968 | 1682 | 2302 | 3210
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0046 | 0.00383 | 0.00786 | 0.00304 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.76572 | 9.4626 | 114.336 | 0.07 | 907 | 1587 | 2183 | 3025
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.03 | 1635 | 2626 | 3435 | 5975
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.035 | 1497 | 2441 | 3219 | 5310
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.04 | 1377 | 2275 | 3022 | 4789
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.045 | 1272 | 2126 | 2843 | 4366
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.05 | 1178 | 1991 | 2679 | 4014
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.055 | 1096 | 1869 | 2529 | 3715
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.06 | 1022 | 1758 | 2392 | 3457
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.065 | 956 | 1658 | 2266 | 3233
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00434 | 0.0036 | 0.0074 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77053 | 9.1767 | 121.536 | 0.07 | 898 | 1566 | 2150 | 3035
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.03 | 1422 | 2307 | 3034 | 3830
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.035 | 1295 | 2132 | 2827 | 3594
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.04 | 1184 | 1977 | 2641 | 3378
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.045 | 1088 | 1838 | 2472 | 3181
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.05 | 1004 | 1713 | 2320 | 3000
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.055 | 930 | 1602 | 2181 | 2835
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.06 | 865 | 1502 | 2055 | 2684
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.065 | 807 | 1411 | 1940 | 2544
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00429 | 0.00356 | 0.00732 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.77535 | 10.1743 | 121.536 | 0.07 | 756 | 1330 | 1836 | 2416
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.03 | 1413 | 2293 | 3016 | 3808
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.035 | 1286 | 2118 | 2809 | 3572
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.04 | 1176 | 1963 | 2624 | 3357
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.045 | 1080 | 1825 | 2456 | 3160
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.05 | 996 | 1701 | 2303 | 2980
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.055 | 922 | 1590 | 2165 | 2816
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.06 | 858 | 1490 | 2040 | 2665
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.065 | 800 | 1400 | 1926 | 2526
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00425 | 0.00353 | 0.00724 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.78199 | 10.2178 | 121.536 | 0.07 | 749 | 1319 | 1822 | 2398
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.03 | 1403 | 2278 | 2997 | 3786
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.035 | 1277 | 2104 | 2792 | 3550
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.04 | 1167 | 1950 | 2606 | 3336
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.045 | 1072 | 1812 | 2439 | 3140
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.05 | 988 | 1689 | 2287 | 2960
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.055 | 915 | 1578 | 2150 | 2796
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.06 | 851 | 1479 | 2025 | 2646
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.065 | 794 | 1389 | 1911 | 2508
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0042 | 0.0035 | 0.00717 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.79062 | 10.2741 | 121.536 | 0.07 | 743 | 1309 | 1808 | 2381
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.03 | 1385 | 2250 | 2962 | 3742
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.035 | 1259 | 2077 | 2757 | 3508
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.04 | 1150 | 1924 | 2573 | 3294
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.045 | 1056 | 1787 | 2406 | 3099
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.05 | 973 | 1664 | 2256 | 2921
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.055 | 901 | 1555 | 2120 | 2758
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.06 | 837 | 1457 | 1996 | 2609
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.065 | 781 | 1368 | 1883 | 2472
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00417 | 0.00345 | 0.00709 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.8049 | 10.3664 | 121.536 | 0.07 | 731 | 1288 | 1780 | 2346
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.03 | 1382 | 2237 | 2938 | 3784
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.035 | 1260 | 2070 | 2741 | 3540
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.04 | 1153 | 1921 | 2563 | 3321
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.045 | 1061 | 1788 | 2402 | 3122
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.05 | 979 | 1668 | 2256 | 2942
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.055 | 908 | 1561 | 2123 | 2778
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.06 | 845 | 1464 | 2002 | 2629
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.065 | 789 | 1377 | 1891 | 2492
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00394 | 0.00329 | 0.00672 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.80219 | 9.9639 | 128.736 | 0.07 | 739 | 1298 | 1790 | 2366
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.03 | 1188 | 1944 | 2568 | 3255
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.035 | 1076 | 1787 | 2382 | 3040
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.04 | 979 | 1649 | 2215 | 2845
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.045 | 896 | 1527 | 2065 | 2668
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.05 | 824 | 1418 | 1930 | 2508
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.055 | 761 | 1321 | 1808 | 2362
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.06 | 706 | 1235 | 1699 | 2228
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.065 | 657 | 1158 | 1599 | 2107
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00392 | 0.00325 | 0.00666 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81503 | 11.1005 | 128.736 | 0.07 | 614 | 1088 | 1509 | 1995
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.03 | 1185 | 1940 | 2563 | 3248
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.035 | 1073 | 1783 | 2376 | 3033
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.04 | 977 | 1645 | 2209 | 2838
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.045 | 893 | 1523 | 2059 | 2662
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.05 | 821 | 1414 | 1925 | 2501
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.055 | 758 | 1318 | 1803 | 2355
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.06 | 703 | 1231 | 1694 | 2222
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.065 | 655 | 1154 | 1595 | 2101
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00387 | 0.00321 | 0.0066 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81784 | 11.1196 | 128.736 | 0.07 | 612 | 1085 | 1505 | 1990
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.03 | 1184 | 1937 | 2560 | 3244
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.035 | 1072 | 1781 | 2373 | 3029
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.04 | 975 | 1643 | 2206 | 2835
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.045 | 892 | 1521 | 2057 | 2658
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.05 | 820 | 1412 | 1922 | 2498
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.055 | 757 | 1316 | 1801 | 2352
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.06 | 702 | 1230 | 1692 | 2219
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.065 | 654 | 1153 | 1593 | 2098
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00653 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.81994 | 11.1339 | 128.736 | 0.07 | 611 | 1083 | 1503 | 1987
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.03 | 1181 | 1933 | 2554 | 3237
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.035 | 1069 | 1776 | 2368 | 3022
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.04 | 973 | 1639 | 2201 | 2828
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.045 | 890 | 1517 | 2051 | 2652
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.05 | 818 | 1408 | 1917 | 2492
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.055 | 755 | 1312 | 1796 | 2346
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.06 | 700 | 1226 | 1687 | 2213
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.065 | 652 | 1149 | 1588 | 2092
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00646 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.82224 | 11.1494 | 128.736 | 0.07 | 610 | 1080 | 1498 | 1981
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.03 | 1176 | 1918 | 2529 | 3201
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.035 | 1067 | 1766 | 2349 | 2994
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.04 | 972 | 1632 | 2188 | 2807
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.045 | 891 | 1514 | 2043 | 2636
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.05 | 820 | 1408 | 1912 | 2481
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.055 | 758 | 1313 | 1794 | 2339
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.06 | 704 | 1229 | 1687 | 2210
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.065 | 656 | 1153 | 1590 | 2091
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00361 | 0.00302 | 0.00617 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83278 | 10.7639 | 135.936 | 0.07 | 614 | 1084 | 1502 | 1982
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.03 | 1015 | 1673 | 2219 | 2821
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.035 | 915 | 1531 | 2049 | 2624
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.04 | 830 | 1407 | 1898 | 2447
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.045 | 756 | 1298 | 1763 | 2287
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.05 | 694 | 1202 | 1643 | 2143
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.055 | 639 | 1117 | 1535 | 2012
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.06 | 592 | 1042 | 1438 | 1894
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.065 | 550 | 974 | 1351 | 1786
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00359 | 0.00297 | 0.0061 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.83718 | 11.9284 | 135.936 | 0.07 | 514 | 914 | 1272 | 1688
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.03 | 1012 | 1667 | 2212 | 2812
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.035 | 911 | 1526 | 2042 | 2615
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.04 | 826 | 1402 | 1891 | 2439
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.045 | 753 | 1293 | 1757 | 2279
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.05 | 691 | 1197 | 1637 | 2135
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.055 | 636 | 1113 | 1529 | 2005
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.06 | 589 | 1037 | 1433 | 1887
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.065 | 548 | 970 | 1346 | 1779
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00356 | 0.00296 | 0.00605 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.8421 | 11.9634 | 135.936 | 0.07 | 511 | 910 | 1267 | 1681
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.03 | 1006 | 1658 | 2200 | 2798
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.035 | 906 | 1517 | 2030 | 2601
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.04 | 821 | 1393 | 1880 | 2425
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.045 | 748 | 1285 | 1746 | 2266
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.05 | 686 | 1190 | 1627 | 2122
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.055 | 632 | 1105 | 1519 | 1992
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.06 | 585 | 1030 | 1423 | 1875
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.065 | 544 | 964 | 1337 | 1768
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00598 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.84837 | 12.0079 | 135.936 | 0.07 | 508 | 904 | 1259 | 1670
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.03 | 999 | 1649 | 2188 | 2783
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.035 | 900 | 1508 | 2019 | 2587
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.04 | 816 | 1385 | 1869 | 2411
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.045 | 743 | 1277 | 1736 | 2253
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.05 | 681 | 1182 | 1616 | 2110
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.055 | 628 | 1098 | 1510 | 1980
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.06 | 581 | 1023 | 1414 | 1863
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.065 | 540 | 957 | 1328 | 1756
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00348 | 0.0029 | 0.00591 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00289 | 0.00289 | 0.00289 | 0.85513 | 12.0556 | 135.936 | 0.07 | 504 | 898 | 1250 | 1660

## 25%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.03 | 3216 | 10690 | 13346 | 14268
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.035 | 3001 | 9273 | 11439 | 12230
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.04 | 2807 | 8196 | 10009 | 10701
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.045 | 2632 | 7348 | 8897 | 9512
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.05 | 2472 | 6661 | 8008 | 8561
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.055 | 2327 | 6093 | 7280 | 7783
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.06 | 2195 | 5614 | 6673 | 7134
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.065 | 2074 | 5205 | 6160 | 6585
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00576 | 0.00477 | 0.00992 | 0.00379 | 0.00251 | 0.00319 | 0.00251 | 0.00339 | 0.00339 | 0.00251 | 0.00251 | 0.00251 | 0.73955 | 6.6849 | 92.736 | 0.07 | 1964 | 4852 | 5720 | 6115
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.03 | 2838 | 7130 | 11096 | 12816
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.035 | 2634 | 6337 | 9584 | 10985
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.04 | 2451 | 5712 | 8440 | 9612
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.045 | 2286 | 5206 | 7544 | 8544
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.05 | 2139 | 4784 | 6822 | 7690
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.055 | 2005 | 4425 | 6227 | 6991
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.06 | 1884 | 4116 | 5728 | 6408
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.065 | 1775 | 3847 | 5302 | 5915
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00569 | 0.00471 | 0.00981 | 0.00375 | 0.00251 | 0.00316 | 0.00251 | 0.00331 | 0.00331 | 0.00251 | 0.00251 | 0.00251 | 0.73932 | 7.3874 | 92.736 | 0.07 | 1676 | 3610 | 4937 | 5493
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.03 | 2838 | 7130 | 11096 | 12816
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.035 | 2634 | 6337 | 9584 | 10985
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.04 | 2451 | 5712 | 8440 | 9612
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.045 | 2286 | 5206 | 7544 | 8544
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.05 | 2139 | 4784 | 6822 | 7690
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.055 | 2005 | 4425 | 6227 | 6991
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.06 | 1884 | 4116 | 5728 | 6408
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.065 | 1775 | 3847 | 5302 | 5915
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00565 | 0.00467 | 0.00971 | 0.00371 | 0.00251 | 0.00313 | 0.00251 | 0.00324 | 0.00324 | 0.00251 | 0.00251 | 0.00251 | 0.73926 | 7.3871 | 92.736 | 0.07 | 1676 | 3610 | 4937 | 5493
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.03 | 2838 | 7130 | 11096 | 12816
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.035 | 2634 | 6337 | 9584 | 10985
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.04 | 2451 | 5712 | 8440 | 9612
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.045 | 2286 | 5206 | 7544 | 8544
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.05 | 2139 | 4784 | 6822 | 7690
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.055 | 2005 | 4425 | 6227 | 6991
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.06 | 1884 | 4116 | 5728 | 6408
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.065 | 1775 | 3847 | 5302 | 5915
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00559 | 0.00461 | 0.00961 | 0.00369 | 0.00251 | 0.00309 | 0.00251 | 0.00315 | 0.00315 | 0.00251 | 0.00251 | 0.00251 | 0.73915 | 7.3866 | 92.736 | 0.07 | 1676 | 3610 | 4937 | 5493
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.03 | 2838 | 7130 | 11096 | 12816
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.035 | 2634 | 6337 | 9584 | 10985
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.04 | 2451 | 5712 | 8440 | 9612
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.045 | 2286 | 5206 | 7544 | 8544
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.05 | 2139 | 4784 | 6822 | 7690
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.055 | 2005 | 4425 | 6227 | 6991
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.06 | 1884 | 4116 | 5728 | 6408
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.065 | 1775 | 3847 | 5302 | 5915
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00554 | 0.00458 | 0.00951 | 0.00365 | 0.00251 | 0.00305 | 0.00251 | 0.00306 | 0.00306 | 0.00251 | 0.00251 | 0.00251 | 0.73908 | 7.3863 | 92.736 | 0.07 | 1676 | 3610 | 4937 | 5493
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.03 | 2692 | 7221 | 10782 | 12124
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.035 | 2501 | 6379 | 9287 | 10392
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.04 | 2330 | 5723 | 8160 | 9093
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.045 | 2175 | 5195 | 7279 | 8083
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.05 | 2036 | 4758 | 6571 | 7274
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.055 | 1910 | 4390 | 5989 | 6613
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.06 | 1797 | 4074 | 5502 | 6062
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.065 | 1693 | 3800 | 5089 | 5596
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00502 | 0.00416 | 0.00864 | 0.00332 | 0.00249 | 0.00279 | 0.00249 | 0.00298 | 0.00298 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 7.2559 | 99.936 | 0.07 | 1599 | 3561 | 4733 | 5196
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.03 | 2373 | 3767 | 7941 | 10825
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.035 | 2192 | 3528 | 6983 | 9282
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.04 | 2031 | 3311 | 6243 | 8124
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.045 | 1887 | 3113 | 5650 | 7224
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.05 | 1759 | 2932 | 5163 | 6503
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.055 | 1644 | 2767 | 4755 | 5914
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.06 | 1541 | 2616 | 4407 | 5422
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.065 | 1448 | 2477 | 4106 | 5005
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00498 | 0.00413 | 0.00855 | 0.00329 | 0.00249 | 0.00276 | 0.00249 | 0.00289 | 0.00289 | 0.00249 | 0.00249 | 0.00249 | 0.73848 | 8.0196 | 99.936 | 0.07 | 1363 | 2350 | 3843 | 4648
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.03 | 2373 | 3767 | 7941 | 10825
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.035 | 2192 | 3528 | 6983 | 9282
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.04 | 2031 | 3311 | 6243 | 8124
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.045 | 1887 | 3113 | 5650 | 7224
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.05 | 1759 | 2932 | 5163 | 6503
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.055 | 1644 | 2767 | 4755 | 5914
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.06 | 1541 | 2616 | 4407 | 5422
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.065 | 1448 | 2477 | 4106 | 5005
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00494 | 0.00409 | 0.00846 | 0.00326 | 0.00249 | 0.00274 | 0.00249 | 0.00282 | 0.00282 | 0.00249 | 0.00249 | 0.00249 | 0.73871 | 8.0209 | 99.936 | 0.07 | 1363 | 2350 | 3843 | 4648
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.03 | 2373 | 3767 | 7941 | 10825
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.035 | 2192 | 3528 | 6983 | 9282
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.04 | 2031 | 3311 | 6243 | 8124
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.045 | 1887 | 3113 | 5650 | 7224
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.05 | 1759 | 2932 | 5163 | 6503
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.055 | 1644 | 2767 | 4755 | 5914
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.06 | 1541 | 2616 | 4407 | 5422
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.065 | 1448 | 2477 | 4106 | 5005
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00487 | 0.00405 | 0.00838 | 0.00323 | 0.00249 | 0.0027 | 0.00249 | 0.00276 | 0.00276 | 0.00249 | 0.00249 | 0.00249 | 0.73882 | 8.0215 | 99.936 | 0.07 | 1363 | 2350 | 3843 | 4648
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.03 | 2373 | 3767 | 7941 | 10825
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.035 | 2192 | 3528 | 6983 | 9282
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.04 | 2031 | 3311 | 6243 | 8124
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.045 | 1887 | 3113 | 5650 | 7224
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.05 | 1759 | 2932 | 5163 | 6503
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.055 | 1644 | 2767 | 4755 | 5914
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.06 | 1541 | 2616 | 4407 | 5422
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.065 | 1448 | 2477 | 4106 | 5005
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00484 | 0.004 | 0.00829 | 0.00319 | 0.00249 | 0.00269 | 0.00249 | 0.00269 | 0.00269 | 0.00249 | 0.00249 | 0.00249 | 0.73908 | 8.0229 | 99.936 | 0.07 | 1363 | 2350 | 3843 | 4648
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.03 | 2279 | 4218 | 8035 | 10389
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.035 | 2108 | 3874 | 7023 | 8905
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.04 | 1955 | 3582 | 6246 | 7792
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.045 | 1819 | 3331 | 5630 | 6926
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.05 | 1697 | 3110 | 5127 | 6233
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.055 | 1588 | 2915 | 4708 | 5667
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.06 | 1489 | 2741 | 4352 | 5195
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.065 | 1400 | 2584 | 4047 | 4795
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00445 | 0.0037 | 0.00763 | 0.00295 | 0.00247 | 0.00247 | 0.00247 | 0.00264 | 0.00264 | 0.00248 | 0.00248 | 0.00248 | 0.73949 | 7.8371 | 107.136 | 0.07 | 1319 | 2442 | 3781 | 4452
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.03 | 2000 | 3197 | 5141 | 8237
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.035 | 1839 | 2982 | 4676 | 7182
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.04 | 1697 | 2787 | 4293 | 6376
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.045 | 1571 | 2611 | 3971 | 5738
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.05 | 1459 | 2451 | 3693 | 5218
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.055 | 1360 | 2306 | 3451 | 4787
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.06 | 1271 | 2174 | 3236 | 4421
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.065 | 1191 | 2054 | 3045 | 4107
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0044 | 0.00366 | 0.00755 | 0.00293 | 0.00247 | 0.00247 | 0.00247 | 0.00258 | 0.00258 | 0.00248 | 0.00248 | 0.00248 | 0.74 | 8.6651 | 107.136 | 0.07 | 1120 | 1944 | 2874 | 3836
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.03 | 2000 | 3197 | 5141 | 8237
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.035 | 1839 | 2982 | 4676 | 7182
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.04 | 1697 | 2787 | 4293 | 6376
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.045 | 1571 | 2611 | 3971 | 5738
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.05 | 1459 | 2451 | 3693 | 5218
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.055 | 1360 | 2306 | 3451 | 4787
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.06 | 1271 | 2174 | 3236 | 4421
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.065 | 1191 | 2054 | 3045 | 4107
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00436 | 0.00362 | 0.00747 | 0.00289 | 0.00247 | 0.00247 | 0.00247 | 0.0025 | 0.0025 | 0.00248 | 0.00248 | 0.00248 | 0.74057 | 8.6684 | 107.136 | 0.07 | 1120 | 1944 | 2874 | 3836
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.03 | 2000 | 3197 | 5141 | 8237
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.035 | 1839 | 2982 | 4676 | 7182
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.04 | 1697 | 2787 | 4293 | 6376
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.045 | 1571 | 2611 | 3971 | 5738
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.05 | 1459 | 2451 | 3693 | 5218
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.055 | 1360 | 2306 | 3451 | 4787
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.06 | 1271 | 2174 | 3236 | 4421
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.065 | 1191 | 2054 | 3045 | 4107
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00431 | 0.00359 | 0.0074 | 0.00286 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74147 | 8.6736 | 107.136 | 0.07 | 1120 | 1944 | 2874 | 3836
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.03 | 1997 | 3192 | 5106 | 8209
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.035 | 1836 | 2977 | 4648 | 7159
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.04 | 1694 | 2783 | 4270 | 6357
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.045 | 1568 | 2607 | 3951 | 5722
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.05 | 1457 | 2447 | 3676 | 5205
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.055 | 1357 | 2302 | 3436 | 4776
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.06 | 1268 | 2170 | 3222 | 4412
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.065 | 1189 | 2050 | 3033 | 4099
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00428 | 0.00355 | 0.00732 | 0.00284 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00247 | 0.00248 | 0.00248 | 0.00248 | 0.74265 | 8.6806 | 107.136 | 0.07 | 1117 | 1940 | 2863 | 3828
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.03 | 1942 | 3095 | 5569 | 8335
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.035 | 1788 | 2891 | 4991 | 7219
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.04 | 1652 | 2706 | 4531 | 6373
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.045 | 1531 | 2538 | 4152 | 5708
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.05 | 1424 | 2386 | 3833 | 5171
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.055 | 1328 | 2247 | 3560 | 4727
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.06 | 1243 | 2120 | 3323 | 4354
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.065 | 1166 | 2005 | 3113 | 4035
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00399 | 0.00331 | 0.00683 | 0.00264 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.74453 | 8.4421 | 114.336 | 0.07 | 1096 | 1899 | 2928 | 3761
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.03 | 1698 | 2732 | 3577 | 5923
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.035 | 1554 | 2537 | 3348 | 5304
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.04 | 1428 | 2363 | 3141 | 4813
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.045 | 1317 | 2205 | 2952 | 4410
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.05 | 1219 | 2064 | 2780 | 4071
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.055 | 1133 | 1936 | 2623 | 3780
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.06 | 1056 | 1820 | 2479 | 3528
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.065 | 988 | 1715 | 2347 | 3307
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00395 | 0.00329 | 0.00676 | 0.00261 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7462 | 9.3412 | 114.336 | 0.07 | 927 | 1620 | 2226 | 3111
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.03 | 1695 | 2728 | 3572 | 5896
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.035 | 1551 | 2534 | 3344 | 5283
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.04 | 1425 | 2359 | 3137 | 4796
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.045 | 1315 | 2202 | 2948 | 4396
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.05 | 1217 | 2061 | 2776 | 4059
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.055 | 1131 | 1933 | 2619 | 3770
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.06 | 1055 | 1817 | 2475 | 3519
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.065 | 986 | 1713 | 2343 | 3299
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00391 | 0.00325 | 0.00669 | 0.0026 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.7483 | 9.3544 | 114.336 | 0.07 | 925 | 1617 | 2222 | 3104
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.03 | 1690 | 2721 | 3563 | 5842
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.035 | 1547 | 2527 | 3335 | 5240
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.04 | 1421 | 2352 | 3128 | 4761
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.045 | 1311 | 2196 | 2939 | 4367
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.05 | 1213 | 2054 | 2768 | 4034
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.055 | 1127 | 1927 | 2611 | 3749
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.06 | 1051 | 1812 | 2467 | 3501
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.065 | 983 | 1707 | 2336 | 3283
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00387 | 0.00322 | 0.00663 | 0.00256 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75075 | 9.3697 | 114.336 | 0.07 | 922 | 1612 | 2215 | 3090
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.03 | 1686 | 2714 | 3554 | 5789
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.035 | 1542 | 2520 | 3326 | 5198
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.04 | 1417 | 2345 | 3119 | 4726
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.045 | 1306 | 2189 | 2931 | 4338
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.05 | 1209 | 2048 | 2759 | 4010
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.055 | 1123 | 1921 | 2603 | 3728
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.06 | 1047 | 1806 | 2459 | 3482
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.065 | 979 | 1701 | 2328 | 3266
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00384 | 0.00319 | 0.00655 | 0.00254 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.75399 | 9.3898 | 114.336 | 0.07 | 919 | 1606 | 2208 | 3075
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.03 | 1651 | 2651 | 3467 | 6151
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.035 | 1514 | 2466 | 3250 | 5450
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.04 | 1393 | 2299 | 3052 | 4903
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.045 | 1286 | 2149 | 2872 | 4461
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.05 | 1192 | 2013 | 2707 | 4094
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.055 | 1109 | 1890 | 2557 | 3784
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.06 | 1035 | 1779 | 2418 | 3518
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.065 | 968 | 1677 | 2292 | 3286
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00361 | 0.003 | 0.00616 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.75868 | 9.1059 | 121.536 | 0.07 | 909 | 1585 | 2175 | 3082
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.03 | 1436 | 2328 | 3060 | 3862
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.035 | 1308 | 2152 | 2852 | 3624
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.04 | 1197 | 1996 | 2665 | 3408
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.045 | 1100 | 1856 | 2496 | 3210
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.05 | 1015 | 1731 | 2343 | 3029
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.055 | 940 | 1619 | 2203 | 2863
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.06 | 875 | 1518 | 2077 | 2711
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.065 | 816 | 1427 | 1961 | 2571
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00358 | 0.00296 | 0.0061 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.76344 | 10.0959 | 121.536 | 0.07 | 764 | 1345 | 1856 | 2442
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.03 | 1428 | 2316 | 3045 | 3844
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.035 | 1300 | 2141 | 2838 | 3607
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.04 | 1189 | 1985 | 2651 | 3391
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.045 | 1093 | 1846 | 2482 | 3193
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.05 | 1008 | 1721 | 2329 | 3013
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.055 | 934 | 1609 | 2191 | 2847
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.06 | 869 | 1509 | 2064 | 2695
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.065 | 811 | 1418 | 1949 | 2556
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00354 | 0.00294 | 0.00604 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77018 | 10.1404 | 121.536 | 0.07 | 759 | 1336 | 1844 | 2427
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.03 | 1417 | 2298 | 3023 | 3817
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.035 | 1289 | 2124 | 2817 | 3581
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.04 | 1179 | 1969 | 2630 | 3365
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.045 | 1083 | 1830 | 2462 | 3168
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.05 | 999 | 1706 | 2310 | 2988
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.055 | 925 | 1595 | 2172 | 2824
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.06 | 860 | 1495 | 2046 | 2672
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.065 | 803 | 1405 | 1932 | 2533
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0035 | 0.00291 | 0.00597 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.77922 | 10.1997 | 121.536 | 0.07 | 752 | 1323 | 1827 | 2405
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.03 | 1398 | 2270 | 2987 | 3773
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.035 | 1271 | 2096 | 2781 | 3537
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.04 | 1162 | 1942 | 2596 | 3323
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.045 | 1067 | 1804 | 2429 | 3127
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.05 | 984 | 1681 | 2278 | 2948
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.055 | 911 | 1571 | 2141 | 2785
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.06 | 847 | 1472 | 2016 | 2635
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.065 | 790 | 1383 | 1903 | 2497
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00348 | 0.00288 | 0.00591 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.79506 | 10.3029 | 121.536 | 0.07 | 739 | 1303 | 1799 | 2370
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.03 | 1395 | 2257 | 2964 | 3951
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.035 | 1272 | 2089 | 2766 | 3672
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.04 | 1165 | 1940 | 2587 | 3428
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.045 | 1072 | 1806 | 2425 | 3212
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.05 | 990 | 1686 | 2278 | 3018
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.055 | 918 | 1578 | 2145 | 2844
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.06 | 855 | 1481 | 2023 | 2686
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.065 | 798 | 1393 | 1912 | 2542
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00329 | 0.00274 | 0.0056 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.7911 | 9.8947 | 128.736 | 0.07 | 748 | 1313 | 1810 | 2410
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.03 | 1199 | 1960 | 2589 | 3280
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.035 | 1086 | 1803 | 2402 | 3064
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.04 | 989 | 1664 | 2234 | 2869
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.045 | 905 | 1541 | 2083 | 2691
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.05 | 832 | 1432 | 1948 | 2530
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.055 | 769 | 1334 | 1826 | 2383
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.06 | 713 | 1247 | 1715 | 2249
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.065 | 664 | 1170 | 1615 | 2127
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00326 | 0.00271 | 0.00555 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80536 | 11.0344 | 128.736 | 0.07 | 621 | 1099 | 1524 | 2015
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.03 | 1196 | 1956 | 2583 | 3273
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.035 | 1083 | 1799 | 2396 | 3057
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.04 | 986 | 1660 | 2228 | 2862
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.045 | 902 | 1537 | 2078 | 2685
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.05 | 830 | 1428 | 1943 | 2524
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.055 | 766 | 1331 | 1821 | 2377
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.06 | 711 | 1244 | 1710 | 2243
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.065 | 662 | 1166 | 1611 | 2121
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00323 | 0.00267 | 0.0055 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.80828 | 11.0544 | 128.736 | 0.07 | 619 | 1096 | 1520 | 2009
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.03 | 1193 | 1951 | 2577 | 3266
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.035 | 1080 | 1794 | 2390 | 3050
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.04 | 983 | 1655 | 2223 | 2855
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.045 | 900 | 1533 | 2073 | 2678
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.05 | 827 | 1424 | 1937 | 2517
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.055 | 764 | 1327 | 1816 | 2371
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.06 | 709 | 1240 | 1706 | 2237
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.065 | 660 | 1163 | 1606 | 2115
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.8103 | 11.0682 | 128.736 | 0.07 | 617 | 1093 | 1516 | 2004
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.03 | 1191 | 1949 | 2574 | 3262
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.035 | 1079 | 1792 | 2387 | 3047
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.04 | 982 | 1653 | 2220 | 2852
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.045 | 898 | 1531 | 2070 | 2675
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.05 | 826 | 1422 | 1935 | 2514
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.055 | 763 | 1325 | 1813 | 2368
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.06 | 708 | 1239 | 1703 | 2234
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.065 | 659 | 1161 | 1604 | 2112
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00316 | 0.00262 | 0.00539 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.00243 | 0.81253 | 11.0834 | 128.736 | 0.07 | 616 | 1091 | 1513 | 2001
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.03 | 1185 | 1932 | 2547 | 3222
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.035 | 1075 | 1780 | 2367 | 3015
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.04 | 981 | 1645 | 2205 | 2827
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.045 | 899 | 1526 | 2059 | 2656
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.05 | 828 | 1420 | 1928 | 2500
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.055 | 765 | 1325 | 1809 | 2358
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.06 | 711 | 1240 | 1702 | 2228
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.065 | 662 | 1163 | 1604 | 2109
| 36 | 16 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00514 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82293 | 10.7001 | 135.936 | 0.07 | 620 | 1094 | 1515 | 1999
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.03 | 1024 | 1686 | 2236 | 2842
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.035 | 923 | 1544 | 2065 | 2644
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.04 | 837 | 1419 | 1913 | 2466
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.045 | 764 | 1310 | 1778 | 2306
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.05 | 700 | 1213 | 1657 | 2161
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.055 | 645 | 1128 | 1549 | 2030
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.06 | 598 | 1052 | 1452 | 1911
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.065 | 556 | 984 | 1364 | 1803
| 36 | 16 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00299 | 0.00247 | 0.00509 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.82738 | 11.8584 | 135.936 | 0.07 | 519 | 923 | 1285 | 1704
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.03 | 1020 | 1680 | 2228 | 2833
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.035 | 920 | 1538 | 2058 | 2635
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.04 | 834 | 1414 | 1907 | 2458
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.045 | 761 | 1305 | 1772 | 2298
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.05 | 697 | 1208 | 1651 | 2153
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.055 | 643 | 1123 | 1543 | 2022
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.06 | 595 | 1047 | 1446 | 1904
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.065 | 553 | 980 | 1358 | 1795
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00296 | 0.00246 | 0.00504 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.83243 | 11.8945 | 135.936 | 0.07 | 517 | 919 | 1279 | 1697
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.03 | 1014 | 1671 | 2216 | 2818
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.035 | 914 | 1529 | 2046 | 2621
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.04 | 828 | 1405 | 1896 | 2444
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.045 | 755 | 1297 | 1761 | 2284
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.05 | 693 | 1201 | 1641 | 2140
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.055 | 638 | 1116 | 1533 | 2010
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.06 | 591 | 1040 | 1436 | 1891
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.065 | 549 | 973 | 1349 | 1784
| 36 | 16 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00293 | 0.00244 | 0.00499 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.839 | 11.9414 | 135.936 | 0.07 | 513 | 913 | 1271 | 1686
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.03 | 1008 | 1662 | 2204 | 2803
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.035 | 908 | 1520 | 2035 | 2607
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.04 | 823 | 1397 | 1884 | 2430
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.045 | 750 | 1288 | 1750 | 2271
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.05 | 688 | 1193 | 1631 | 2127
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.055 | 634 | 1108 | 1523 | 1997
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.06 | 587 | 1033 | 1427 | 1879
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.065 | 545 | 966 | 1340 | 1772
| 36 | 16 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00492 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.84622 | 11.9927 | 135.936 | 0.07 | 509 | 907 | 1262 | 1675

## thickness_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.03 | 4256 | 16158 | 17451 | 18546
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.035 | 3992 | 13866 | 14958 | 15897
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.04 | 3751 | 12146 | 13088 | 13910
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.045 | 3531 | 10807 | 11634 | 12364
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.05 | 3330 | 9733 | 10470 | 11128
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.055 | 3146 | 8855 | 9518 | 10116
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.06 | 2977 | 8121 | 8725 | 9273
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.065 | 2822 | 7500 | 8054 | 8560
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00621 | 0.00515 | 0.01083 | 0.00408 | 0.00206 | 0.00342 | 0.00206 | 0.00352 | 0.00352 | 0.00206 | 0.00206 | 0.00206 | 0.73306 | 6.0887 | 78.336 | 0.07 | 2680 | 6967 | 7479 | 7948
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.03 | 4041 | 14924 | 16626 | 17697
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.035 | 3786 | 12837 | 14251 | 15169
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.04 | 3553 | 11266 | 12470 | 13273
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.045 | 3341 | 10040 | 11084 | 11798
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.05 | 3148 | 9055 | 9976 | 10618
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.055 | 2971 | 8248 | 9069 | 9653
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.06 | 2809 | 7572 | 8313 | 8848
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.065 | 2661 | 6999 | 7674 | 8168
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00594 | 0.00493 | 0.01034 | 0.0039 | 0.00205 | 0.00326 | 0.00205 | 0.00338 | 0.00338 | 0.00205 | 0.00205 | 0.00205 | 0.732 | 6.2425 | 80.136 | 0.07 | 2524 | 6507 | 7126 | 7584
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.03 | 3834 | 13688 | 15827 | 16873
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.035 | 3587 | 11806 | 13566 | 14462
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.04 | 3362 | 10385 | 11870 | 12655
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.045 | 3158 | 9273 | 10551 | 11248
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.05 | 2972 | 8378 | 9496 | 10124
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.055 | 2802 | 7641 | 8633 | 9203
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.06 | 2647 | 7024 | 7913 | 8436
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.065 | 2505 | 6499 | 7305 | 7787
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00569 | 0.00472 | 0.00988 | 0.00374 | 0.00204 | 0.00313 | 0.00204 | 0.00324 | 0.00324 | 0.00204 | 0.00204 | 0.00204 | 0.73107 | 6.3967 | 81.936 | 0.07 | 2375 | 6047 | 6783 | 7231
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.03 | 3648 | 12561 | 15103 | 16125
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.035 | 3408 | 10865 | 12945 | 13821
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.04 | 3191 | 9581 | 11327 | 12094
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.045 | 2994 | 8572 | 10068 | 10750
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.05 | 2815 | 7758 | 9062 | 9675
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.055 | 2652 | 7086 | 8238 | 8795
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.06 | 2503 | 6522 | 7551 | 8063
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.065 | 2367 | 6041 | 6970 | 7442
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00546 | 0.00453 | 0.00945 | 0.00359 | 0.00204 | 0.003 | 0.00204 | 0.00311 | 0.00311 | 0.00204 | 0.00204 | 0.00204 | 0.73024 | 6.5512 | 83.736 | 0.07 | 2242 | 5626 | 6473 | 6911
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.03 | 3467 | 11426 | 14399 | 15398
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.035 | 3236 | 9919 | 12342 | 13198
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.04 | 3026 | 8773 | 10799 | 11548
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.045 | 2836 | 7869 | 9599 | 10265
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.05 | 2664 | 7136 | 8639 | 9239
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.055 | 2507 | 6530 | 7854 | 8399
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.06 | 2364 | 6019 | 7199 | 7699
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.065 | 2234 | 5582 | 6645 | 7107
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00525 | 0.00435 | 0.00906 | 0.00344 | 0.00203 | 0.0029 | 0.00203 | 0.00299 | 0.00299 | 0.00203 | 0.00203 | 0.00203 | 0.72952 | 6.706 | 85.536 | 0.07 | 2115 | 5204 | 6171 | 6599
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.03 | 3305 | 10392 | 13760 | 14737
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.035 | 3080 | 9056 | 11794 | 12631
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.04 | 2878 | 8034 | 10320 | 11053
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.045 | 2694 | 7226 | 9173 | 9824
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.05 | 2528 | 6568 | 8256 | 8842
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.055 | 2377 | 6021 | 7505 | 8038
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.06 | 2240 | 5558 | 6880 | 7368
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.065 | 2115 | 5162 | 6351 | 6802
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00505 | 0.00418 | 0.00872 | 0.00331 | 0.00202 | 0.00278 | 0.00202 | 0.00288 | 0.00288 | 0.00202 | 0.00202 | 0.00202 | 0.7289 | 6.8612 | 87.336 | 0.07 | 2001 | 4818 | 5897 | 6316
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.03 | 3148 | 9348 | 13095 | 14092
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.035 | 2930 | 8184 | 11228 | 12079
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.04 | 2734 | 7290 | 9827 | 10569
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.045 | 2557 | 6578 | 8738 | 9395
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.05 | 2396 | 5995 | 7865 | 8455
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.055 | 2251 | 5508 | 7153 | 7687
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.06 | 2120 | 5095 | 6558 | 7046
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.065 | 2000 | 4739 | 6054 | 6504
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00838 | 0.00319 | 0.00202 | 0.00268 | 0.00202 | 0.00277 | 0.00277 | 0.00202 | 0.00202 | 0.00202 | 0.72834 | 7.0165 | 89.136 | 0.07 | 1891 | 4430 | 5622 | 6039
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.03 | 3005 | 8396 | 12220 | 13505
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.035 | 2794 | 7390 | 10507 | 11575
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.04 | 2604 | 6611 | 9218 | 10128
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.045 | 2433 | 5985 | 8212 | 9003
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.05 | 2279 | 5472 | 7405 | 8103
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.055 | 2139 | 5040 | 6743 | 7366
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.06 | 2012 | 4671 | 6190 | 6752
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.065 | 1897 | 4352 | 5720 | 6233
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00468 | 0.00388 | 0.00807 | 0.00309 | 0.00201 | 0.00259 | 0.00201 | 0.00268 | 0.00268 | 0.00202 | 0.00202 | 0.00202 | 0.72793 | 7.1724 | 90.936 | 0.07 | 1793 | 4074 | 5317 | 5788
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.03 | 2867 | 7431 | 11338 | 12930
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.035 | 2662 | 6585 | 9780 | 11083
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.045 | 2313 | 5387 | 7683 | 8620
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.05 | 2164 | 4942 | 6941 | 7758
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.055 | 2030 | 4566 | 6332 | 7053
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.06 | 1908 | 4243 | 5821 | 6465
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.065 | 1798 | 3961 | 5386 | 5968
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.07 | 1698 | 3714 | 5012 | 5542
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.03 | 2742 | 6551 | 10529 | 12407
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.035 | 2543 | 5851 | 9113 | 10634
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.04 | 2365 | 5295 | 8039 | 9305
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.045 | 2205 | 4840 | 7197 | 8271
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.05 | 2061 | 4459 | 6516 | 7444
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.055 | 1932 | 4133 | 5954 | 6767
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.06 | 1814 | 3851 | 5481 | 6203
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.065 | 1709 | 3604 | 5079 | 5726
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00436 | 0.00361 | 0.0075 | 0.00288 | 0.00201 | 0.00241 | 0.00201 | 0.00249 | 0.00249 | 0.002 | 0.002 | 0.002 | 0.72726 | 7.4848 | 94.536 | 0.07 | 1612 | 3387 | 4731 | 5317
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.03 | 2619 | 5657 | 9712 | 11893
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.035 | 2426 | 5104 | 8440 | 10194
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.04 | 2254 | 4657 | 7470 | 8920
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.045 | 2099 | 4285 | 6706 | 7929
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.05 | 1961 | 3968 | 6086 | 7136
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.055 | 1836 | 3694 | 5573 | 6487
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.06 | 1723 | 3454 | 5140 | 5947
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.065 | 1622 | 3242 | 4769 | 5489
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00421 | 0.00348 | 0.00724 | 0.00278 | 0.002 | 0.00233 | 0.002 | 0.00241 | 0.00241 | 0.002 | 0.002 | 0.002 | 0.72705 | 7.6416 | 96.336 | 0.07 | 1530 | 3053 | 4448 | 5097
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.03 | 2504 | 4795 | 8924 | 11408
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.035 | 2317 | 4386 | 7790 | 9778
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.04 | 2150 | 4043 | 6922 | 8556
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.045 | 2001 | 3750 | 6234 | 7605
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.05 | 1867 | 3496 | 5673 | 6845
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.055 | 1747 | 3272 | 5206 | 6222
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.06 | 1638 | 3072 | 4811 | 5704
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.065 | 1541 | 2894 | 4471 | 5265
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00408 | 0.00337 | 0.007 | 0.00269 | 0.00199 | 0.00226 | 0.00199 | 0.00234 | 0.00234 | 0.002 | 0.002 | 0.002 | 0.72704 | 7.7994 | 98.136 | 0.07 | 1452 | 2733 | 4176 | 4889
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.03 | 2396 | 3964 | 8166 | 10948
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.035 | 2214 | 3692 | 7165 | 9384
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.045 | 1908 | 3235 | 5779 | 7299
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.05 | 1779 | 3040 | 5275 | 6569
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.055 | 1663 | 2864 | 4852 | 5972
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.06 | 1559 | 2703 | 4493 | 5474
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.065 | 1465 | 2557 | 4183 | 5053
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.07 | 1380 | 2424 | 3913 | 4692
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.03 | 2294 | 3645 | 7433 | 10332
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.035 | 2118 | 3412 | 6562 | 8878
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.04 | 1961 | 3200 | 5885 | 7786
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.045 | 1821 | 3007 | 5340 | 6934
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.05 | 1696 | 2831 | 4890 | 6251
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.055 | 1585 | 2670 | 4511 | 5691
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.06 | 1484 | 2523 | 4187 | 5223
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.065 | 1394 | 2388 | 3906 | 4826
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00382 | 0.00317 | 0.00655 | 0.00253 | 0.00199 | 0.00212 | 0.00199 | 0.0022 | 0.0022 | 0.00199 | 0.00199 | 0.00199 | 0.72726 | 8.1164 | 101.736 | 0.07 | 1313 | 2265 | 3659 | 4486
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.03 | 2198 | 3499 | 6727 | 9678
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.035 | 2027 | 3271 | 5980 | 8348
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.04 | 1874 | 3065 | 5393 | 7344
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.045 | 1739 | 2877 | 4916 | 6559
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.05 | 1619 | 2707 | 4519 | 5926
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.055 | 1511 | 2551 | 4182 | 5406
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.06 | 1414 | 2409 | 3892 | 4970
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.065 | 1328 | 2279 | 3638 | 4599
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00635 | 0.00245 | 0.00198 | 0.00206 | 0.00198 | 0.00213 | 0.00213 | 0.00198 | 0.00198 | 0.00198 | 0.72759 | 8.2762 | 103.536 | 0.07 | 1249 | 2160 | 3415 | 4280
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.03 | 2107 | 3360 | 6044 | 9047
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.035 | 1941 | 3138 | 5417 | 7836
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.04 | 1793 | 2937 | 4917 | 6918
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.045 | 1662 | 2755 | 4506 | 6196
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.05 | 1546 | 2590 | 4161 | 5612
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.055 | 1442 | 2439 | 3864 | 5131
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.06 | 1349 | 2302 | 3606 | 4726
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.065 | 1265 | 2176 | 3379 | 4380
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00359 | 0.00298 | 0.00616 | 0.00238 | 0.00198 | 0.002 | 0.00198 | 0.00207 | 0.00207 | 0.00198 | 0.00198 | 0.00198 | 0.7281 | 8.4371 | 105.336 | 0.07 | 1190 | 2061 | 3178 | 4081
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.03 | 2022 | 3229 | 5385 | 8438
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.035 | 1860 | 3013 | 4874 | 7341
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.045 | 1590 | 2640 | 4111 | 5845
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.05 | 1477 | 2480 | 3814 | 5310
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.055 | 1377 | 2334 | 3557 | 4866
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.06 | 1287 | 2201 | 3330 | 4490
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.065 | 1207 | 2079 | 3130 | 4168
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.07 | 1135 | 1968 | 2950 | 3890
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.03 | 1941 | 3104 | 4747 | 7848
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.035 | 1783 | 2894 | 4348 | 6863
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.04 | 1644 | 2703 | 4014 | 6107
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.045 | 1521 | 2531 | 3729 | 5506
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.05 | 1413 | 2376 | 3480 | 5017
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.055 | 1316 | 2234 | 3260 | 4608
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.06 | 1229 | 2105 | 3063 | 4262
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.065 | 1152 | 1988 | 2888 | 3963
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00339 | 0.00282 | 0.00581 | 0.00225 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.72993 | 8.7641 | 108.936 | 0.07 | 1082 | 1881 | 2730 | 3704
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.03 | 1861 | 2983 | 4096 | 7250
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.035 | 1708 | 2777 | 3812 | 6377
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.04 | 1573 | 2592 | 3562 | 5704
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.045 | 1455 | 2425 | 3339 | 5164
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.05 | 1349 | 2274 | 3139 | 4720
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.055 | 1256 | 2137 | 2958 | 4348
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.06 | 1173 | 2012 | 2793 | 4031
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.065 | 1098 | 1899 | 2643 | 3757
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.0033 | 0.00274 | 0.00564 | 0.00219 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.73146 | 8.9317 | 110.736 | 0.07 | 1032 | 1795 | 2506 | 3517
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.03 | 1786 | 2867 | 3749 | 6671
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.035 | 1637 | 2667 | 3515 | 5908
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.04 | 1507 | 2487 | 3301 | 5313
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.045 | 1391 | 2324 | 3106 | 4832
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.05 | 1290 | 2177 | 2928 | 4434
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.055 | 1200 | 2045 | 2765 | 4098
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.06 | 1119 | 1924 | 2616 | 3808
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.065 | 1048 | 1815 | 2479 | 3557
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00321 | 0.00267 | 0.00549 | 0.00213 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.7334 | 9.1022 | 112.536 | 0.07 | 984 | 1715 | 2353 | 3337
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.03 | 1712 | 2754 | 3604 | 6084
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.035 | 1568 | 2559 | 3376 | 5432
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.04 | 1441 | 2383 | 3168 | 4917
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.045 | 1330 | 2226 | 2978 | 4497
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.05 | 1232 | 2083 | 2805 | 4144
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.055 | 1145 | 1955 | 2647 | 3843
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.06 | 1067 | 1838 | 2502 | 3583
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.065 | 999 | 1733 | 2370 | 3355
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.07 | 937 | 1637 | 2248 | 3154
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.03 | 1645 | 2650 | 3472 | 5540
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.035 | 1505 | 2460 | 3248 | 4992
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.04 | 1382 | 2289 | 3045 | 4551
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.045 | 1274 | 2136 | 2861 | 4185
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.05 | 1179 | 1998 | 2693 | 3875
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.055 | 1095 | 1873 | 2539 | 3608
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.06 | 1020 | 1760 | 2399 | 3374
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.065 | 954 | 1658 | 2270 | 3168
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00305 | 0.00254 | 0.00522 | 0.00202 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73889 | 9.4546 | 116.136 | 0.07 | 895 | 1565 | 2152 | 2985
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.03 | 1577 | 2545 | 3338 | 4962
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.035 | 1440 | 2360 | 3119 | 4523
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.04 | 1321 | 2194 | 2922 | 4162
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.045 | 1217 | 2045 | 2742 | 3855
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.05 | 1125 | 1911 | 2579 | 3591
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.055 | 1044 | 1790 | 2430 | 3359
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.06 | 973 | 1681 | 2294 | 3154
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.065 | 909 | 1583 | 2169 | 2970
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00298 | 0.00247 | 0.00508 | 0.00197 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.7428 | 9.6392 | 117.936 | 0.07 | 852 | 1493 | 2056 | 2806
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.03 | 1511 | 2443 | 3206 | 4376
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.035 | 1378 | 2262 | 2993 | 4050
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.04 | 1263 | 2100 | 2801 | 3769
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.045 | 1162 | 1956 | 2626 | 3522
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.05 | 1073 | 1826 | 2467 | 3304
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.055 | 995 | 1710 | 2323 | 3108
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.06 | 927 | 1604 | 2191 | 2931
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.065 | 865 | 1509 | 2071 | 2772
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.0029 | 0.00241 | 0.00495 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00196 | 0.00196 | 0.00196 | 0.74852 | 9.8365 | 119.736 | 0.07 | 811 | 1423 | 1961 | 2626
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.03 | 1446 | 2343 | 3078 | 3884
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.035 | 1317 | 2166 | 2871 | 3647
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.04 | 1205 | 2010 | 2683 | 3430
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.045 | 1108 | 1869 | 2513 | 3231
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.05 | 1023 | 1744 | 2359 | 3050
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.055 | 948 | 1631 | 2219 | 2883
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.06 | 882 | 1530 | 2092 | 2730
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.065 | 823 | 1438 | 1976 | 2590
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.07 | 771 | 1355 | 1870 | 2460
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.03 | 1377 | 2237 | 2943 | 3718
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.035 | 1253 | 2066 | 2741 | 3486
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.04 | 1145 | 1913 | 2558 | 3274
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.045 | 1051 | 1778 | 2394 | 3082
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.05 | 969 | 1657 | 2245 | 2905
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.055 | 898 | 1548 | 2110 | 2744
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.06 | 834 | 1451 | 1987 | 2596
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.065 | 778 | 1363 | 1875 | 2460
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.76978 | 10.3003 | 123.336 | 0.07 | 729 | 1284 | 1773 | 2336
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.03 | 1315 | 2140 | 2819 | 3565
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.035 | 1194 | 1974 | 2622 | 3338
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.04 | 1090 | 1826 | 2445 | 3132
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.045 | 1000 | 1695 | 2285 | 2945
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.05 | 921 | 1578 | 2140 | 2774
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.055 | 852 | 1473 | 2010 | 2617
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.06 | 791 | 1379 | 1891 | 2474
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.065 | 738 | 1295 | 1784 | 2343
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.0027 | 0.00225 | 0.0046 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.78099 | 10.5387 | 125.136 | 0.07 | 691 | 1219 | 1685 | 2223
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.03 | 1253 | 2044 | 2696 | 3412
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.035 | 1136 | 1882 | 2504 | 3192
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.04 | 1036 | 1739 | 2332 | 2991
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.045 | 949 | 1612 | 2177 | 2809
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.05 | 873 | 1499 | 2037 | 2643
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.055 | 807 | 1398 | 1911 | 2492
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.06 | 749 | 1308 | 1797 | 2353
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.065 | 698 | 1227 | 1693 | 2227
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00264 | 0.00219 | 0.0045 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00195 | 0.00195 | 0.00195 | 0.79475 | 10.7963 | 126.936 | 0.07 | 653 | 1154 | 1599 | 2111
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.03 | 1207 | 1972 | 2604 | 3298
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.035 | 1093 | 1814 | 2416 | 3082
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.04 | 996 | 1675 | 2248 | 2886
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.045 | 911 | 1551 | 2097 | 2708
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.05 | 838 | 1442 | 1961 | 2546
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.055 | 774 | 1344 | 1838 | 2399
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.06 | 719 | 1257 | 1727 | 2264
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.065 | 669 | 1178 | 1627 | 2142
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.07 | 626 | 1108 | 1536 | 2029
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.03 | 1162 | 1902 | 2513 | 3185
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.035 | 1051 | 1748 | 2329 | 2974
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.04 | 956 | 1612 | 2165 | 2782
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.045 | 875 | 1492 | 2018 | 2609
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.05 | 804 | 1385 | 1886 | 2451
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.055 | 743 | 1290 | 1767 | 2308
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.06 | 689 | 1206 | 1659 | 2177
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.065 | 641 | 1130 | 1562 | 2058
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80151 | 11.1739 | 130.536 | 0.07 | 599 | 1062 | 1473 | 1949
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.03 | 1117 | 1832 | 2424 | 3075
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.035 | 1010 | 1682 | 2244 | 2868
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.04 | 918 | 1550 | 2084 | 2681
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.045 | 839 | 1433 | 1941 | 2511
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.05 | 771 | 1330 | 1812 | 2358
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.055 | 711 | 1238 | 1697 | 2218
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.06 | 659 | 1156 | 1592 | 2091
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.065 | 614 | 1083 | 1498 | 1976
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.80641 | 11.3743 | 132.336 | 0.07 | 573 | 1017 | 1413 | 1870
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.03 | 1073 | 1762 | 2333 | 2963
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.035 | 968 | 1616 | 2158 | 2760
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.04 | 879 | 1487 | 2002 | 2578
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.045 | 803 | 1374 | 1863 | 2413
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.05 | 737 | 1274 | 1738 | 2264
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.055 | 680 | 1185 | 1626 | 2128
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.06 | 630 | 1106 | 1525 | 2005
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.065 | 586 | 1035 | 1434 | 1893
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00242 | 0.00201 | 0.00412 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.81275 | 11.586 | 134.136 | 0.07 | 547 | 972 | 1351 | 1790
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.03 | 1030 | 1696 | 2248 | 2856
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.035 | 929 | 1553 | 2077 | 2659
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.04 | 843 | 1428 | 1925 | 2480
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.045 | 769 | 1318 | 1789 | 2320
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.05 | 705 | 1221 | 1668 | 2174
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.055 | 650 | 1135 | 1559 | 2043
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.06 | 602 | 1059 | 1461 | 1923
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.065 | 560 | 991 | 1373 | 1814
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00237 | 0.00197 | 0.00403 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.82128 | 11.8146 | 135.936 | 0.07 | 523 | 930 | 1294 | 1715

## drop_panel_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | hdrop | heff | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | *Assumes drop panels are 1/6 length of span in each direction
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | in | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 15 | 12.9 | 150 | 0 | 80 | 11 | 0.00452 | 0.00227 | 0.00464 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00196 | 0.00196 | 0.00201 | 0.00201 | 0.00201 | 0.75091 | 8.0711 | 98.0285 | 0.04 | 2052 | 3348 | 6235 | 8181
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 16 | 13.2 | 150 | 0 | 80 | 11 | 0.00452 | 0.00196 | 0.00402 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00195 | 0.00195 | 0.00201 | 0.00201 | 0.00201 | 0.74649 | 8.2557 | 99.7927 | 0.04 | 1951 | 3189 | 5644 | 7656
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 17 | 13.5 | 150 | 0 | 80 | 11 | 0.00452 | 0.00194 | 0.00351 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00194 | 0.00194 | 0.00201 | 0.00201 | 0.00201 | 0.74787 | 8.4721 | 101.5569 | 0.04 | 1849 | 3030 | 5022 | 7111
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 16.25 | 13.975 | 150 | 0 | 80 | 11 | 0.00395 | 0.00199 | 0.00408 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00195 | 0.00195 | 0.00199 | 0.00199 | 0.00199 | 0.75104 | 8.7663 | 105.6696 | 0.04 | 1691 | 2781 | 4112 | 6273
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 17 | 14.2 | 150 | 0 | 80 | 11 | 0.00395 | 0.00194 | 0.00368 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00194 | 0.00194 | 0.00199 | 0.00199 | 0.00199 | 0.75001 | 8.917 | 106.9927 | 0.04 | 1630 | 2686 | 3709 | 5920
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 18 | 14.5 | 150 | 0 | 80 | 11 | 0.00395 | 0.00193 | 0.00325 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00193 | 0.00193 | 0.00199 | 0.00199 | 0.00199 | 0.7605 | 9.1898 | 108.7569 | 0.04 | 1536 | 2537 | 3370 | 5330
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 17.5 | 15.05 | 150 | 0 | 80 | 11 | 0.00349 | 0.00194 | 0.00362 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.00194 | 0.00194 | 0.00198 | 0.00198 | 0.00198 | 0.7546 | 9.4833 | 113.3106 | 0.04 | 1409 | 2336 | 3108 | 4611
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 18 | 15.2 | 150 | 0 | 80 | 11 | 0.00349 | 0.00193 | 0.0034 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.00193 | 0.00193 | 0.00198 | 0.00198 | 0.00198 | 0.75661 | 9.601 | 114.1927 | 0.04 | 1373 | 2278 | 3033 | 4367
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 19 | 15.5 | 150 | 0 | 80 | 11 | 0.00349 | 0.00192 | 0.00302 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.00192 | 0.00192 | 0.00198 | 0.00198 | 0.00198 | 0.78467 | 9.9914 | 115.9569 | 0.04 | 1274 | 2122 | 2833 | 3633
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 12 | 12 | 150 | 0 | 80 | 11 | 0.00452 | 0.00374 | 0.00777 | 0.00297 | 0.00201 | 0.0025 | 0.00201 | 0.00259 | 0.00259 | 0.00201 | 0.00201 | 0.00201 | 0.72755 | 7.3284 | 92.736 | 0.04 | 2478 | 5922 | 8603 | 9698
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 13 | 13 | 150 | 0 | 80 | 11 | 0.00395 | 0.00327 | 0.00677 | 0.00261 | 0.00199 | 0.00219 | 0.00199 | 0.00226 | 0.00226 | 0.00199 | 0.00199 | 0.00199 | 0.72708 | 7.9575 | 99.936 | 0.04 | 2052 | 3451 | 6394 | 8211
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00598 | 0.00231 | 0.00198 | 0.00198 | 0.00198 | 0.002 | 0.002 | 0.00198 | 0.00198 | 0.00198 | 0.72882 | 8.5993 | 107.136 | 0.04 | 1717 | 2817 | 4458 | 6505
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 15 | 15 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00535 | 0.00208 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.73577 | 9.2757 | 114.336 | 0.04 | 1441 | 2383 | 3168 | 4917
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 16 | 16 | 150 | 0 | 80 | 11 | 0.00283 | 0.00235 | 0.00483 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.75692 | 10.0527 | 121.536 | 0.04 | 1205 | 2010 | 2683 | 3430
| 36 | 16 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 17 | 17 | 150 | 0 | 80 | 11 | 0.00258 | 0.00214 | 0.0044 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.79779 | 10.9824 | 128.736 | 0.04 | 996 | 1675 | 2248 | 2886