## Slab_Properties
References:
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span |  |  |  | CRSI Design Guide for Vibration of Reinforced Concrete Floor Systems, First Edition
l2 = | 34 | ft | interior |  |  |  |  | ACI 318-14 Building Code Requirements for Structural Concrete
l1 / l2 = | 1 |  | * must be < 2.0, otherwise exhibits one way behavior |  |  |  |  | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
c1 = | 28 | in
c2 = | 28 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 14 | in |  | in | Drop panel: | h = | 14 | in | hdrop = | 14 | in | dextent = | 0.33 | % of span |  | hequiv = | 14 | in
d = | 12.75 | in | *single layer of reinforcement
wc = | 150 | pcf
yt = | 7 | in
n = | 5.6374
lcw = | 1 |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = | 318.1981 | psi | * reduced modulus of rupture, per CRSI Design Guide p4-6
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 175 | psf
mass = | 6677.5155 | lb sec2/ft
weight = | 215.016 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 338 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1440.4903 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1440.4903 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 749.0549 | k-ft
M1n1u = | 374.5275 | k-ft
M1n2u = | 1008.3432 | k-ft
M2pu = | 504.1716 | k-ft
M2n1u = | 936.3187 | k-ft
M2n2u = | 936.3187 | k-ft
Service Moments
M01,DL = | 745.816 | k-ft | *includes SDL and self-weight
M01,LL = | 340.9444 | k-ft
M02,DL = | 745.816 | k-ft
M02,LL = | 340.9444 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 232.6946 | 155.1297 | k-ft
l1 | DL | n1 | 193.9122 | 0 | k-ft
l1 | DL | n2 | 391.5534 | 121.1951 | k-ft
l1 | LL | p | 106.3747 | 70.9164 | k-ft
l1 | LL | n1 | 88.6456 | 0 | k-ft
l1 | LL | n2 | 178.9958 | 59.6653 | k-ft
l2 | DL | p | 156.6214 | 104.4142 | k-ft
l2 | DL | n1 | 363.5853 | 121.1951 | k-ft
l2 | DL | n2 | 363.5853 | 121.1951 | k-ft
l2 | LL | p | 71.5983 | 47.7322 | k-ft
l2 | LL | n1 | 166.2104 | 55.4035 | k-ft
l2 | LL | n2 | 166.2104 | 55.4035 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 449.433 | 299.622 | k-ft
l1 | n1 | 374.5275 | 0 | k-ft
l1 | n2 | 756.2574 | 240.8986 | k-ft
l2 | p | 302.503 | 201.6686 | k-ft
l2 | n1 | 702.239 | 234.0797 | k-ft
l2 | n2 | 702.239 | 234.0797 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation (may be unconservative… ): | [6 empty] | User input (As from rho): |  |  |  |  | User input (rho):
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle
l1 | p | 7.2828 | 5.202 | in2 | l1 | p | 6.6583 | 6.5025 | in2 | l1 | p | 7.2828 | 5.202 |  | l1 | p | 0.0028 | 0.002
l1 | n1 | 5.9823 | 5.202 | in2 | l1 | n1 | 6.5025 | 6.5025 | in2 | l1 | n1 | 5.9823 | 5.202 |  | l1 | n1 | 0.0023 | 0.002
l1 | n2 | 12.2247 | 5.202 | in2 | l1 | n2 | 11.2038 | 6.5025 | in2 | l1 | n2 | 12.2247 | 5.202 |  | l1 | n2 | 0.0047 | 0.002
l2 | p | 5.202 | 5.202 | in2 | l2 | p | 6.5025 | 6.5025 | in2 | l2 | p | 5.202 | 5.202 |  | l2 | p | 0.002 | 0.002
l2 | n1 | 11.4444 | 5.202 | in2 | l2 | n1 | 10.4035 | 6.5025 | in2 | l2 | n1 | 11.4444 | 5.202 |  | l2 | n1 | 0.0044 | 0.002
l2 | n2 | 11.4444 | 5.202 | in2 | l2 | n2 | 10.4035 | 6.5025 | in2 | l2 | n2 | 11.4444 | 5.202 |  | l2 | n2 | 0.0044 | 0.002
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 46648 | 46648 | in3
l1 | n1 | 46648 | 46648 | in3
l1 | n2 | 46648 | 46648 | in3
l2 | p | 46648 | 46648 | in3
l2 | n1 | 46648 | 46648 | in3
l2 | n2 | 46648 | 46648 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 6962.9267 | 8889.0198 | in3 | 4.9688 | 6.9563 | 2.0731 | 1.7762 | 5286.1129 | 3912.6022 | 176.706 | 176.706 | 0.52115 | 0.78173 | 0.0336 | 0.024
l1 | n1 | 6866.7251 | 46648 | in3 | 6.049 | 6.9563 | 1.8945 | 1.7762 | 4436.5646 | 3912.6022 | 176.706 | 176.706 | 0.62538 | 1.1 | 0.0276 | 0.024
l1 | n2 | 9005.0698 | 31181.4061 | in3 | 2.9601 | 6.9563 | 2.6166 | 1.7762 | 8294.8856 | 3912.6022 | 176.706 | 176.706 | 0.30971 | 0.97703 | 0.0564 | 0.024
l2 | p | 8679.7408 | 46648 | in3 | 6.9563 | 6.9563 | 1.7762 | 1.7762 | 3912.6022 | 3912.6022 | 176.706 | 176.706 | 0.77428 | 1.1614 | 0.024 | 0.024
l2 | n1 | 8639.409 | 46648 | in3 | 3.162 | 6.9563 | 2.5411 | 1.7762 | 7839.8329 | 3912.6022 | 176.706 | 176.706 | 0.33354 | 1.0006 | 0.0528 | 0.024
l2 | n2 | 8639.409 | 46648 | in3 | 3.162 | 6.9563 | 2.5411 | 1.7762 | 7839.8329 | 3912.6022 | 176.706 | 176.706 | 0.33354 | 1.0006 | 0.0528 | 0.024
Calculate avg strip Ie
Direction | Column | Middle
l1 | 7254.8179 | 17896.7248 | in3
l2 | 8667.6413 | 46648 | in3
Calculate Panel Ie
Iep = | 53902.8179 | in3
Calculate Panel Ig
Igp = | 93296 | in3
Calculate k1
k1 = | 0.57776
Calculate fi |  |  | Interp li2
k2 = | 2.1 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 5.7764 | slug / ft2 | 2 | 9.29
fi = | 6.5787 | Hz
Calculate/Input Parameters for DG11
W = | 215016 | lb
b = | 0.04

## Drop_Slab_Properties
References:
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span |  |  |  | CRSI Design Guide for Vibration of Reinforced Concrete Floor Systems, First Edition
l2 = | 34 | ft | interior |  |  |  |  | ACI 318-14 Building Code Requirements for Structural Concrete
l1 / l2 = | 1 |  | * must be < 2.0, otherwise exhibits one way behavior |  |  |  |  | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
c1 = | 28 | in
c2 = | 28 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 15.1667 | in | 12 | in | Drop panel: | h = | 14 | in | hdrop = | 17.5 | in | dextent = | 0.33333 | % of span |  | hequiv = | 15.1667 | in
d = | 12.75 | in | *single layer of reinforcement
ddrop = | 16.25 | in
wc = | 150 | pcf
yt = | 7 | in
yt,drop = | 8.75 | in
n = | 5.6374
lcw = | 1 |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = | 318.1981 | psi | * reduced modulus of rupture, per CRSI Design Guide p4-6
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 189.5833 | psf
mass = | 7201.0663 | lb sec2/ft
weight = | 231.8743 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 355.5 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1515.0719 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1515.0719 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 787.8374 | k-ft
M1n1u = | 393.9187 | k-ft
M1n2u = | 1060.5503 | k-ft
M2pu = | 530.2752 | k-ft
M2n1u = | 984.7967 | k-ft
M2n2u = | 984.7967 | k-ft
Service Moments
M01,DL = | 807.9673 | k-ft | *includes SDL and self-weight
M01,LL = | 340.9444 | k-ft
M02,DL = | 807.9673 | k-ft
M02,LL = | 340.9444 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 252.0858 | 168.0572 | k-ft
l1 | DL | n1 | 210.0715 | 0 | k-ft
l1 | DL | n2 | 424.1828 | 141.3943 | k-ft
l1 | LL | p | 106.3747 | 70.9164 | k-ft
l1 | LL | n1 | 88.6456 | 0 | k-ft
l1 | LL | n2 | 178.9958 | 59.6653 | k-ft
l2 | DL | p | 169.6731 | 113.1154 | k-ft
l2 | DL | n1 | 393.8841 | 131.2947 | k-ft
l2 | DL | n2 | 393.8841 | 131.2947 | k-ft
l2 | LL | p | 71.5983 | 47.7322 | k-ft
l2 | LL | n1 | 166.2104 | 55.4035 | k-ft
l2 | LL | n2 | 166.2104 | 55.4035 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 472.7024 | 315.135 | k-ft
l1 | n1 | 393.9187 | 0 | k-ft
l1 | n2 | 795.4127 | 265.1376 | k-ft
l2 | p | 318.1651 | 212.1101 | k-ft
l2 | n1 | 738.5975 | 246.1992 | k-ft
l2 | n2 | 738.5975 | 246.1992 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation (may be unconservative… ): | [6 empty] | User input (As from rho): |  |  |  |  | User input (rho):
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle
l1 | p | 8.4272 | 5.5922 | in2 | l1 | p | 7.003 | 6.5025 | in2 | l1 | p | 8.4272 | 5.5922 |  | l1 | p | 0.00324 | 0.00215
l1 | n1 | 6.4311 | 5.15 | in2 | l1 | n1 | 8.2875 | 6.5025 | in2 | l1 | n1 | 6.4311 | 5.15 |  | l1 | n1 | 0.00194 | 0.00198
l1 | n2 | 11.1384 | 5.15 | in2 | l1 | n2 | 9.2458 | 6.5025 | in2 | l1 | n2 | 11.1384 | 5.15 |  | l1 | n2 | 0.00336 | 0.00198
l2 | p | 5.6442 | 5.15 | in2 | l2 | p | 6.5025 | 6.5025 | in2 | l2 | p | 5.6442 | 5.15 |  | l2 | p | 0.00217 | 0.00198
l2 | n1 | 10.3428 | 5.15 | in2 | l2 | n1 | 8.5854 | 6.5025 | in2 | l2 | n1 | 10.3428 | 5.15 |  | l2 | n1 | 0.00312 | 0.00198
l2 | n2 | 10.3428 | 5.15 | in2 | l2 | n2 | 8.5854 | 6.5025 | in2 | l2 | n2 | 10.3428 | 5.15 |  | l2 | n2 | 0.00312 | 0.00198
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 46648 | 46648 | in3
l1 | n1 | 91109.375 | 46648 | in3
l1 | n2 | 91109.375 | 46648 | in3
l2 | p | 46648 | 46648 | in3
l2 | n1 | 91109.375 | 46648 | in3
l2 | n2 | 91109.375 | 46648 | in3
Calculate avg strip Ig
| Column | Middle
l1 | 59986.4125 | 46648
l2 | 59986.4125 | 46648
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 7632.8954 | 8315.7449 | in3 | 4.294 | 6.471 | 2.2151 | 1.8366 | 6011.7035 | 4176.0024 | 177 | 176.706 | 0.49378 | 0.73944 | 0.03888 | 0.0258
l1 | n1 | 35890.0361 | 46648 | in3 | 5.6268 | 7.0266 | 2.2322 | 1.768 | 7880.3573 | 3877.2605 | 276.1031 | 176.706 | 0.9243 | 1.1 | 0.029671 | 0.02376
l1 | n2 | 15668.9344 | 13288.1987 | in3 | 3.2488 | 7.0266 | 2.87 | 1.768 | 12848.7984 | 3877.2605 | 276.1031 | 176.706 | 0.45775 | 0.87887 | 0.051388 | 0.02376
l2 | p | 8224.1243 | 46648 | in3 | 6.4113 | 7.0266 | 1.8444 | 1.768 | 4210.9052 | 3877.2605 | 176.706 | 176.706 | 0.73239 | 1.0986 | 0.02604 | 0.02376
l2 | n1 | 15258.0224 | 21704.928 | in3 | 3.4987 | 7.0266 | 2.7754 | 1.768 | 12040.1976 | 3877.2605 | 276.1031 | 176.706 | 0.49296 | 0.94648 | 0.047718 | 0.02376
l2 | n2 | 15258.0224 | 21704.928 | in3 | 3.4987 | 7.0266 | 2.7754 | 1.768 | 12040.1976 | 3877.2605 | 276.1031 | 176.706 | 0.49296 | 0.94648 | 0.047718 | 0.02376
Calculate avg strip Ie
Direction | Column | Middle
l1 | 13076.8723 | 14811.4512 | in3
l2 | 10334.2937 | 39165.0784 | in3
Calculate Panel Ie
Iep = | 38693.8479 | in3
Calculate Panel Ig
Igp = | 106634.4125 | in3
Calculate k1
k1 = | 0.36286
Calculate fi |  |  | Interp li2
k2 = | 2.1 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 6.2293 | slug / ft2 | 2 | 9.29
fi = | 5.661 | Hz
Calculate/Input Parameters for DG11
W = | 231874.3333 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits | [7 empty] | References:
fn= | 5.48 | Hz | [5 empty] | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
W = | 231874.3333 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips | Velocity
Very Slow | 5.48 | 1.25 | - | - | - | - | - | 1448.4955 | - | 1448.4955 | - | 1448.4955 | mips
Slow | 5.48 | 1.6 | 6.8 | 6 | 8 | 0.1 | 4659.5258 | 2281.0838 | 4227.3973 | 1430.9355 | N/A | 4659.5258 | mips | * does not consider mode scaling
Moderate | 5.48 | 1.85 | 8 | 7 | 9 | 0.09 | 4921.9938 | 2952.7151 | 3798.1388 | 1624.6169 | N/A | 4921.9938 | mips
Fast | 5.48 | 2.1 | 8.8 | 8 | 10 | 0.08 | 5199.2464 | 3680.9273 | 3517.4823 | 1808.7387 | N/A | 5199.2464 | mips

## Sample_Slabs
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips

## SSM_Example
Slab properties: |  |  | bay type
l1 = | 35 | ft | exterior | * must be larger span
l2 = | 22 | ft | interior
l1 / l2 = | 1.5909 |  | * must be < 2.0
c1 = | 21 | in
c2 = | 21 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 4889136.8257 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 11 | in
d = | 9.75 | in
wc = | 145 | pcf
yt = | 5.5 | in
n = | 5.9315
lcw = | 0.85
fr = | 270.4683 | psi
Strip widths
Direction | Column | Middle
l1 | 11 | 11 | ft | * needs to be adjusted for exterior spans?
l2 | 11 | 24 | ft
Loading
SDL = | 21 | psf
LL = | 125 | psf
LLvib = | 11 | psf
Self weight = | 132.9167 | psf
mass = | 3943.6594 | lb sec2/ft
weight = | 126.9858 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 384.7 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1169.6022 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 690.1608 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 608.1931 | k-ft
M1n1u = | 304.0966 | k-ft
M1n2u = | 818.7215 | k-ft
M2pu = | 241.5563 | k-ft
M2n1u = | 448.6045 | k-ft
M2n2u = | 448.6045 | k-ft
Service Moments
M01,DL = | 467.9524 | k-ft
M01,LL = | 380.0371 | k-ft
M02,DL = | 276.1301 | k-ft
M02,LL = | 224.2529 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 146.0011 | 97.3341 | k-ft
l1 | DL | n1 | 121.6676 | 0 | k-ft
l1 | DL | n2 | 245.675 | 76.0423 | k-ft
l1 | LL | p | 118.5716 | 79.0477 | k-ft
l1 | LL | n1 | 98.8096 | 0 | k-ft
l1 | LL | n2 | 199.5195 | 66.5065 | k-ft
l2 | DL | p | 57.9873 | 38.6582 | k-ft
l2 | DL | n1 | 134.6134 | 44.8711 | k-ft
l2 | DL | n2 | 134.6134 | 44.8711 | k-ft
l2 | LL | p | 47.0931 | 31.3954 | k-ft
l2 | LL | n1 | 109.3233 | 36.4411 | k-ft
l2 | LL | n2 | 109.3233 | 36.4411 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 364.9159 | 243.2773 | k-ft
l1 | n1 | 304.0966 | 0 | k-ft
l1 | n2 | 614.0412 | 197.6611 | k-ft
l2 | p | 144.9338 | 96.6225 | k-ft
l2 | n1 | 336.4534 | 112.1511 | k-ft
l2 | n2 | 336.4534 | 112.1511 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | User input:
l1 | p | 7.0696 | 4.7131 | in2 | l1 | p | 7.0696 | 4.7131 | in2
l1 | n1 | 5.8913 | 3.2175 | in2 | l1 | n1 | 5.8913 | 3.2175 | in2
l1 | n2 | 11.896 | 3.8293 | in2 | l1 | n2 | 11.896 | 3.8293 | in2
l2 | p | 3.2175 | 7.02 | in2 | l2 | p | 3.2175 | 7.02 | in2
l2 | n1 | 6.5182 | 7.02 | in2 | l2 | n1 | 6.5182 | 7.02 | in2
l2 | n2 | 6.5182 | 7.02 | in2 | l2 | n2 | 6.5182 | 7.02 | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 14641 | 14641 | in3
l1 | n1 | 14641 | 14641 | in3
l1 | n2 | 14641 | 14641 | in3
l2 | p | 14641 | 31944 | in3
l2 | n1 | 14641 | 31944 | in3
l2 | n2 | 14641 | 31944 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 2982.2197 | 2247.3153 | in3 | 3.1478 | 4.7218 | 2.1914 | 1.8314 | 2858.7979 | 2023.2082 | 59.9989 | 59.9989 | 0.22678 | 0.34016 | 0.065917 | 0.043945
l1 | n1 | 2611.7399 | 14641 | in3 | 3.7774 | 6.9166 | 2.0227 | 1.5407 | 2450.7004 | 1447.0836 | 59.9989 | 59.9989 | 0.27213 | 1.1 | 0.054931 | 0.03
l1 | n2 | 4428.9103 | 2001.5362 | in3 | 1.8707 | 5.8115 | 2.738 | 1.6678 | 4372.492 | 1687.826 | 59.9989 | 59.9989 | 0.13477 | 0.4209 | 0.11092 | 0.035705
l2 | p | 2049.1012 | 31944 | in3 | 6.9166 | 6.9166 | 1.5407 | 1.5407 | 1447.0836 | 3157.2734 | 59.9989 | 130.9067 | 0.57098 | 1.8687 | 0.03 | 0.03
l2 | n1 | 2808.998 | 31944 | in3 | 3.4141 | 6.9166 | 2.1149 | 1.5407 | 2670.0536 | 3157.2734 | 59.9989 | 130.9067 | 0.24596 | 1.6099 | 0.060776 | 0.03
l2 | n2 | 2808.998 | 31944 | in3 | 3.4141 | 6.9166 | 2.1149 | 1.5407 | 2670.0536 | 3157.2734 | 59.9989 | 130.9067 | 0.24596 | 1.6099 | 0.060776 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 3143.6513 | 4069.5011 | in3
l2 | 2277.0702 | 31944 | in3
Calculate Panel Ie
Iep = | 20717.1113 | in3
Calculate Panel Ig
Igp = | 37933.5 | in3
Calculate k1
k1 = | 0.54614
Calculate fi |  |  | Interp li2
k2 = | 1.9 |  | 1 | 7.12
li2 = | 8.9873 |  | 1.5 | 8.92
g = | 5.1216 | slug / ft2 | 2 | 9.29
fi = | 4.9705 | Hz
Calculate/Input Parameters for DG11
W = | 126985.8333 | lb
b = | 0.03