## Slab_Properties
References:
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span |  |  |  | CRSI Design Guide for Vibration of Reinforced Concrete Floor Systems, First Edition
l2 = | 34 | ft | interior |  |  |  |  | ACI 318-14 Building Code Requirements for Structural Concrete
l1 / l2 = | 1 |  | * must be < 2.0, otherwise exhibits one way behavior |  |  |  |  | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
c1 = | 24 | in
c2 = | 24 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 12 | in
d = | 10.75 | in | *single layer of reinforcement
wc = | 150 | pcf
yt = | 6 | in
n = | 5.6374
lcw = | 1 |  | *lightweight concrete factor, ACI 318-14, 19.2.4.2
fr = | 318.1981 | psi | * reduced modulus of rupture, per CRSI Design Guide p4-6
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 150 | psf
mass = | 5780 | lb sec2/ft
weight = | 186.116 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 308 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1340.416 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1340.416 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 697.0163 | k-ft
M1n1u = | 348.5082 | k-ft
M1n2u = | 938.2912 | k-ft
M2pu = | 469.1456 | k-ft
M2n1u = | 871.2704 | k-ft
M2n2u = | 871.2704 | k-ft
Service Moments
M01,DL = | 652.8 | k-ft | *includes SDL and self-weight
M01,LL = | 348.16 | k-ft
M02,DL = | 652.8 | k-ft
M02,LL = | 348.16 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 203.6736 | 135.7824 | k-ft
l1 | DL | n1 | 169.728 | 0 | k-ft
l1 | DL | n2 | 342.72 | 106.08 | k-ft
l1 | LL | p | 108.6259 | 72.4173 | k-ft
l1 | LL | n1 | 90.5216 | 0 | k-ft
l1 | LL | n2 | 182.784 | 60.928 | k-ft
l2 | DL | p | 137.088 | 91.392 | k-ft
l2 | DL | n1 | 318.24 | 106.08 | k-ft
l2 | DL | n2 | 318.24 | 106.08 | k-ft
l2 | LL | p | 73.1136 | 48.7424 | k-ft
l2 | LL | n1 | 169.728 | 56.576 | k-ft
l2 | LL | n2 | 169.728 | 56.576 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 418.2098 | 278.8065 | k-ft
l1 | n1 | 348.5082 | 0 | k-ft
l1 | n2 | 703.7184 | 224.7808 | k-ft
l2 | p | 281.4874 | 187.6582 | k-ft
l2 | n1 | 653.4528 | 217.8176 | k-ft
l2 | n2 | 653.4528 | 217.8176 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation (may be unconservative… ): | [6 empty] | User input (As from rho): |  |  |  |  | User input (rho):
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Direction | Location | Column | Middle
l1 | p | 7.3465 | 5.4825 | in2 | l1 | p | 7.3484 | 5.4825 | in2 | l1 | p | 7.3465 | 5.4825 |  | l1 | p | 0.00335 | 0.0025
l1 | n1 | 6.1185 | 5.4825 | in2 | l1 | n1 | 6.1237 | 5.4825 | in2 | l1 | n1 | 6.1185 | 5.4825 |  | l1 | n1 | 0.00279 | 0.0025
l1 | n2 | 12.3685 | 5.4825 | in2 | l1 | n2 | 12.3651 | 5.4825 | in2 | l1 | n2 | 12.3685 | 5.4825 |  | l1 | n2 | 0.00564 | 0.0025
l2 | p | 5.4825 | 5.4825 | in2 | l2 | p | 5.4825 | 5.4825 | in2 | l2 | p | 5.4825 | 5.4825 |  | l2 | p | 0.0025 | 0.0025
l2 | n1 | 11.4694 | 5.4825 | in2 | l2 | n1 | 11.4819 | 5.4825 | in2 | l2 | n1 | 11.4694 | 5.4825 |  | l2 | n1 | 0.00523 | 0.0025
l2 | n2 | 11.4694 | 5.4825 | in2 | l2 | n2 | 11.4819 | 5.4825 | in2 | l2 | n2 | 11.4694 | 5.4825 |  | l2 | n2 | 0.00523 | 0.0025
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 29376 | 29376 | in3
l1 | n1 | 29376 | 29376 | in3
l1 | n2 | 29376 | 29376 | in3
l2 | p | 29376 | 29376 | in3
l2 | n1 | 29376 | 29376 | in3
l2 | n2 | 29376 | 29376 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 4369.9861 | 4413.6222 | in3 | 4.9257 | 6.6004 | 1.8961 | 1.6597 | 3710.1817 | 2864.8547 | 129.8248 | 129.8248 | 0.41571 | 0.62356 | 0.0402 | 0.03
l1 | n1 | 4060.0209 | 29376 | in3 | 5.9143 | 6.6004 | 1.745 | 1.6597 | 3158.3144 | 2864.8547 | 129.8248 | 129.8248 | 0.49885 | 1.1 | 0.03348 | 0.03
l1 | n2 | 6100.2845 | 6301.2541 | in3 | 2.9257 | 6.6004 | 2.3905 | 1.6597 | 5801.4964 | 2864.8547 | 129.8248 | 129.8248 | 0.24705 | 0.77736 | 0.06768 | 0.03
l2 | p | 4368.849 | 12708.5009 | in3 | 6.6004 | 6.6004 | 1.6597 | 1.6597 | 2864.8547 | 2864.8547 | 129.8248 | 129.8248 | 0.61762 | 0.92643 | 0.03 | 0.03
l2 | n1 | 5777.1463 | 6739.6414 | in3 | 3.1551 | 6.6004 | 2.3127 | 1.6597 | 5444.002 | 2864.8547 | 129.8248 | 129.8248 | 0.26605 | 0.79816 | 0.06276 | 0.03
l2 | n2 | 5777.1463 | 6739.6414 | in3 | 3.1551 | 6.6004 | 2.3127 | 1.6597 | 5444.002 | 2864.8547 | 129.8248 | 129.8248 | 0.26605 | 0.79816 | 0.06276 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 4583.0361 | 8441.1237 | in3
l2 | 4791.3382 | 10917.8431 | in3
Calculate Panel Ie
Iep = | 15500.8791 | in3
Calculate Panel Ig
Igp = | 58752 | in3
Calculate k1
k1 = | 0.26384
Calculate fi |  |  | Interp li2
k2 = | 1.9 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 5 | slug / ft2 | 2 | 9.29
fi = | 3.4308 | Hz
Calculate/Input Parameters for DG11
W = | 186116 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits | [7 empty] | References:
fn= | 3.4308 | Hz | [5 empty] | AISC Steel Design Guide 11: Vibration of Steel-Framed Structural Systems Due to Human Activity
W = | 186116 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips | Velocity
Very Slow | 3.4308 | 1.25 | - | - | - | - | - | 3128.9122 | - | 3128.9122 | - | 3128.9122 | mips
Slow | 3.4308 | 1.6 | 6.8 | 6 | 8 | 0.1 | 9005.3869 | 4765.8009 | 5266.7419 | 1782.7442 | N/A | 9005.3869 | mips | * does not consider mode scaling
Moderate | 3.4308 | 1.85 | 8 | 7 | 9 | 0.09 | 9319.7017 | 6064.4971 | 4731.9463 | 2024.0439 | N/A | 9319.7017 | mips
Fast | 3.4308 | 2.1 | 8.8 | 8 | 10 | 0.08 | 9644.9869 | 7459.0574 | 4382.2877 | 2253.4337 | N/A | 9644.9869 | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193

## Drop_panel_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | hdrop | heff | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | *Assumes drop panels are 1/6 length of span in each direction
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | in | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 15 | 12.99 | 150 | 0 | 80 | 11
2 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 16 | 13.32 | 150 | 0 | 80 | 11
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 17 | 13.65 | 150 | 0 | 80 | 11
4 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 14 | 11.32 | 150 | 0 | 80 | 11
5 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 15 | 11.65 | 150 | 0 | 80 | 11
6 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 16 | 11.98 | 150 | 0 | 80 | 11
7 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 17.5 | 15.155 | 150 | 0 | 80 | 11
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 18 | 15.32 | 150 | 0 | 80 | 11
9 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 19 | 15.65 | 150 | 0 | 80 | 11
10 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 12 | 12 | 150 | 0 | 80 | 11
11 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 13 | 13 | 150 | 0 | 80 | 11
12 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11
14 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 15 | 15 | 150 | 0 | 80 | 11
15 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 16 | 16 | 150 | 0 | 80 | 11
16 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 17 | 17 | 150 | 0 | 80 | 11

## thickness_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11

## interior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.02 | 3727 | 18285 | 18911 | 19560
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.025 | 3582 | 14628 | 15129 | 15648
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.03 | 3445 | 12190 | 12608 | 13040
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.035 | 3315 | 10448 | 10807 | 11177
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.04 | 3191 | 9142 | 9456 | 9780
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.045 | 3075 | 8127 | 8405 | 8693
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25425 | 3.3679 | 186.116 | 0.05 | 2964 | 7314 | 7565 | 7824
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.02 | 3309 | 16456 | 17095 | 17759
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.025 | 3165 | 13165 | 13676 | 14207
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.03 | 3030 | 10971 | 11397 | 11840
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.035 | 2902 | 9404 | 9769 | 10148
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.04 | 2783 | 8228 | 8548 | 8880
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.045 | 2670 | 7314 | 7598 | 7893
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.26665 | 3.8121 | 186.116 | 0.05 | 2563 | 6583 | 6838 | 7104
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.02 | 3226 | 16083 | 16724 | 17391
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.025 | 3082 | 12866 | 13379 | 13913
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.03 | 2947 | 10722 | 11149 | 11594
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.035 | 2821 | 9190 | 9557 | 9938
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.04 | 2702 | 8041 | 8362 | 8696
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.045 | 2590 | 7148 | 7433 | 7729
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28102 | 3.9134 | 186.116 | 0.05 | 2484 | 6433 | 6690 | 6956
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.02 | 3131 | 15653 | 16296 | 16967
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.025 | 2988 | 12522 | 13037 | 13573
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.03 | 2854 | 10435 | 10864 | 11311
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.035 | 2728 | 8944 | 9312 | 9695
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.04 | 2610 | 7826 | 8148 | 8483
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.045 | 2499 | 6957 | 7243 | 7541
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29873 | 4.0349 | 186.116 | 0.05 | 2394 | 6261 | 6519 | 6787
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.02 | 3005 | 15074 | 15721 | 16395
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.025 | 2863 | 12059 | 12577 | 13116
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.03 | 2729 | 10049 | 10481 | 10930
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.035 | 2605 | 8614 | 8983 | 9369
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.04 | 2488 | 7537 | 7860 | 8198
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.045 | 2378 | 6700 | 6987 | 7287
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32336 | 4.1979 | 186.116 | 0.05 | 2276 | 6030 | 6288 | 6558
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.02 | 2308 | 11691 | 12298 | 12936
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.025 | 2179 | 9353 | 9838 | 10349
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.03 | 2060 | 7794 | 8198 | 8624
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.035 | 1950 | 6681 | 7027 | 7392
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.04 | 1848 | 5845 | 6149 | 6468
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.045 | 1754 | 5196 | 5466 | 5749
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48565 | 5.0558 | 200.566 | 0.05 | 1666 | 4676 | 4919 | 5174
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.02 | 2076 | 10529 | 11135 | 11777
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.025 | 1950 | 8423 | 8908 | 9421
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.03 | 1833 | 7019 | 7423 | 7851
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.035 | 1727 | 6016 | 6363 | 6729
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.04 | 1629 | 5264 | 5568 | 5888
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.045 | 1540 | 4679 | 4949 | 5234
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48845 | 5.6041 | 200.566 | 0.05 | 1457 | 4212 | 4454 | 4711
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.02 | 2069 | 10489 | 11095 | 11737
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.025 | 1942 | 8391 | 8876 | 9389
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.03 | 1826 | 6993 | 7397 | 7825
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.035 | 1720 | 5994 | 6340 | 6707
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.04 | 1622 | 5245 | 5548 | 5868
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.045 | 1532 | 4662 | 4931 | 5216
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.49179 | 5.6232 | 200.566 | 0.05 | 1450 | 4196 | 4438 | 4695
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.02 | 2061 | 10449 | 11056 | 11697
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.025 | 1934 | 8360 | 8845 | 9358
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.03 | 1818 | 6966 | 7371 | 7798
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.035 | 1712 | 5971 | 6318 | 6684
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.04 | 1615 | 5225 | 5528 | 5849
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.045 | 1525 | 4644 | 4914 | 5199
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.4955 | 5.6444 | 200.566 | 0.05 | 1443 | 4180 | 4422 | 4679
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.02 | 2049 | 10391 | 10997 | 11638
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.025 | 1923 | 8312 | 8797 | 9311
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.03 | 1807 | 6927 | 7331 | 7759
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.035 | 1701 | 5937 | 6284 | 6650
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.04 | 1604 | 5195 | 5498 | 5819
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.045 | 1515 | 4618 | 4887 | 5173
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.50012 | 5.6706 | 200.566 | 0.05 | 1433 | 4156 | 4399 | 4655
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.02 | 1867 | 9462 | 10027 | 10625
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.025 | 1749 | 7569 | 8021 | 8500
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.03 | 1642 | 6308 | 6684 | 7084
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.035 | 1544 | 5407 | 5729 | 6072
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.04 | 1454 | 4731 | 5013 | 5313
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.045 | 1372 | 4205 | 4456 | 4722
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.54903 | 5.8023 | 215.016 | 0.05 | 1297 | 3785 | 4011 | 4250
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.02 | 1643 | 7235 | 8849 | 9446
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.025 | 1528 | 5859 | 7079 | 7557
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.03 | 1425 | 4933 | 5899 | 6297
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.035 | 1332 | 4265 | 5056 | 5398
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.04 | 1247 | 3760 | 4424 | 4723
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.045 | 1171 | 3363 | 3933 | 4198
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.56896 | 6.5284 | 215.016 | 0.05 | 1101 | 3043 | 3539 | 3778
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.02 | 1600 | 6667 | 8617 | 9213
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.025 | 1486 | 5426 | 6894 | 7371
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.03 | 1384 | 4588 | 5745 | 6142
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.035 | 1292 | 3980 | 4924 | 5265
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.04 | 1208 | 3518 | 4309 | 4607
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.045 | 1132 | 3155 | 3830 | 4095
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.597 | 6.6874 | 215.016 | 0.05 | 1064 | 2860 | 3447 | 3685
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.02 | 1600 | 6667 | 8617 | 9213
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.025 | 1486 | 5426 | 6894 | 7371
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.03 | 1384 | 4588 | 5745 | 6142
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.035 | 1292 | 3980 | 4924 | 5265
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.04 | 1208 | 3518 | 4309 | 4607
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.045 | 1132 | 3155 | 3830 | 4095
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.59808 | 6.6934 | 215.016 | 0.05 | 1064 | 2860 | 3447 | 3685
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.02 | 1597 | 6631 | 8603 | 9199
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.025 | 1484 | 5399 | 6882 | 7359
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.03 | 1381 | 4566 | 5735 | 6133
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.035 | 1289 | 3962 | 4916 | 5257
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.04 | 1206 | 3503 | 4302 | 4600
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.045 | 1130 | 3142 | 3824 | 4089
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.59916 | 6.6994 | 215.016 | 0.05 | 1061 | 2849 | 3441 | 3680
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.02 | 1531 | 6678 | 8248 | 8808
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.025 | 1424 | 5413 | 6599 | 7046
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.03 | 1328 | 4561 | 5499 | 5872
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.035 | 1241 | 3946 | 4713 | 5033
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.04 | 1162 | 3480 | 4124 | 4404
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.045 | 1090 | 3114 | 3666 | 3914
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.60879 | 6.5593 | 229.466 | 0.05 | 1024 | 2819 | 3299 | 3523
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.02 | 1367 | 4315 | 6926 | 7904
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.025 | 1263 | 3611 | 5580 | 6324
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.03 | 1170 | 3123 | 4678 | 5270
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.035 | 1087 | 2759 | 4030 | 4517
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.04 | 1012 | 2477 | 3541 | 3952
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.045 | 945 | 2249 | 3159 | 3513
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.61151 | 7.2659 | 229.466 | 0.05 | 885 | 2061 | 2852 | 3162
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.02 | 1364 | 4282 | 6898 | 7893
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.025 | 1261 | 3586 | 5559 | 6314
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.03 | 1168 | 3103 | 4661 | 5262
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.035 | 1085 | 2743 | 4017 | 4510
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.04 | 1010 | 2463 | 3530 | 3946
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.045 | 943 | 2237 | 3150 | 3508
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.61472 | 7.285 | 229.466 | 0.05 | 883 | 2050 | 2844 | 3157
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.02 | 1358 | 4182 | 6815 | 7858
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.025 | 1255 | 3510 | 5497 | 6286
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.03 | 1162 | 3042 | 4612 | 5238
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.035 | 1079 | 2693 | 3977 | 4490
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.04 | 1005 | 2421 | 3497 | 3929
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.045 | 938 | 2200 | 3122 | 3492
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.61835 | 7.3064 | 229.466 | 0.05 | 878 | 2018 | 2820 | 3143
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.02 | 1354 | 4116 | 6760 | 7834
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.025 | 1250 | 3459 | 5455 | 6267
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.03 | 1158 | 3002 | 4580 | 5223
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.035 | 1075 | 2659 | 3951 | 4477
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.04 | 1001 | 2392 | 3475 | 3917
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.045 | 934 | 2176 | 3103 | 3482
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.62211 | 7.3286 | 229.466 | 0.05 | 874 | 1997 | 2804 | 3134
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.02 | 1298 | 4248 | 6674 | 7505
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.025 | 1200 | 3541 | 5367 | 6004
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.03 | 1112 | 3053 | 4492 | 5003
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.035 | 1034 | 2691 | 3866 | 4288
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.04 | 963 | 2410 | 3394 | 3752
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.045 | 900 | 2185 | 3026 | 3335
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.64429 | 7.2102 | 243.916 | 0.05 | 842 | 1999 | 2730 | 3002
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.02 | 1152 | 1772 | 4586 | 6666
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.025 | 1057 | 1653 | 3804 | 5334
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.03 | 974 | 1545 | 3268 | 4446
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.035 | 899 | 1447 | 2873 | 3812
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.04 | 833 | 1358 | 2568 | 3336
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.045 | 774 | 1277 | 2323 | 2965
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.65156 | 8.014 | 243.916 | 0.05 | 722 | 1203 | 2122 | 2669
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.02 | 1142 | 1758 | 4429 | 6532
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.025 | 1048 | 1639 | 3687 | 5235
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.03 | 964 | 1531 | 3176 | 4371
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.035 | 890 | 1434 | 2799 | 3752
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.04 | 825 | 1345 | 2506 | 3287
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.045 | 766 | 1264 | 2271 | 2925
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.6605 | 8.0688 | 243.916 | 0.05 | 714 | 1191 | 2077 | 2635
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.02 | 1132 | 1744 | 4273 | 6398
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.025 | 1038 | 1625 | 3570 | 5137
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.03 | 955 | 1518 | 3084 | 4296
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.035 | 882 | 1421 | 2724 | 3692
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.04 | 816 | 1332 | 2444 | 3238
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.045 | 758 | 1252 | 2218 | 2884
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.67126 | 8.1342 | 243.916 | 0.05 | 706 | 1178 | 2031 | 2601
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.02 | 1120 | 1725 | 4064 | 6219
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.025 | 1026 | 1607 | 3414 | 5006
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.03 | 943 | 1500 | 2961 | 4195
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.035 | 870 | 1403 | 2625 | 3613
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.04 | 805 | 1315 | 2361 | 3173
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.045 | 747 | 1235 | 2148 | 2830
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.6839 | 8.2104 | 243.916 | 0.05 | 696 | 1162 | 1971 | 2555
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.02 | 1042 | 1607 | 3589 | 5659
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.025 | 954 | 1496 | 3038 | 4571
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.03 | 876 | 1395 | 2651 | 3841
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.035 | 808 | 1304 | 2360 | 3315
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.04 | 747 | 1222 | 2131 | 2918
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.045 | 693 | 1147 | 1945 | 2608
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.75541 | 8.3079 | 258.366 | 0.05 | 645 | 1079 | 1788 | 2357
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.02 | 901 | 1402 | 1803 | 3360
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.025 | 817 | 1295 | 1681 | 2887
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.03 | 745 | 1199 | 1570 | 2549
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.035 | 681 | 1113 | 1469 | 2290
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.04 | 626 | 1036 | 1378 | 2083
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.045 | 577 | 967 | 1295 | 1913
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.79108 | 9.3967 | 258.366 | 0.05 | 534 | 905 | 1219 | 1768
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.02 | 867 | 1352 | 1741 | 2707
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.025 | 784 | 1245 | 1619 | 2408
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.03 | 713 | 1151 | 1510 | 2181
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.035 | 651 | 1066 | 1410 | 1998
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.04 | 596 | 991 | 1320 | 1845
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.045 | 549 | 923 | 1239 | 1715
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.84419 | 9.707 | 258.366 | 0.05 | 508 | 863 | 1165 | 1601
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.02 | 847 | 1324 | 1706 | 2327
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.025 | 766 | 1218 | 1585 | 2130
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.03 | 695 | 1124 | 1476 | 1967
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.035 | 634 | 1041 | 1378 | 1829
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.04 | 580 | 966 | 1289 | 1707
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.045 | 534 | 899 | 1208 | 1600
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.87622 | 9.8894 | 258.366 | 0.05 | 493 | 840 | 1135 | 1503
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.02 | 847 | 1324 | 1706 | 2327
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.025 | 766 | 1218 | 1585 | 2130
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.03 | 695 | 1124 | 1476 | 1967
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.035 | 634 | 1041 | 1378 | 1829
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.04 | 580 | 966 | 1289 | 1707
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.045 | 534 | 899 | 1208 | 1600
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.87607 | 9.8886 | 258.366 | 0.05 | 493 | 840 | 1135 | 1503
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.02 | 845 | 1315 | 1693 | 3023
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.025 | 766 | 1214 | 1577 | 2618
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.03 | 697 | 1123 | 1472 | 2324
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.035 | 637 | 1043 | 1377 | 2098
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.04 | 585 | 970 | 1291 | 1915
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.045 | 540 | 905 | 1212 | 1763
| 34 | 34 | interior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.87578 | 9.4845 | 272.816 | 0.05 | 499 | 846 | 1141 | 1634
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.02 | 748 | 1173 | 1516 | 1887
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.025 | 672 | 1075 | 1403 | 1760
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.03 | 608 | 989 | 1302 | 1646
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.035 | 552 | 912 | 1211 | 1542
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.04 | 504 | 844 | 1130 | 1447
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.045 | 463 | 784 | 1056 | 1361
| 34 | 34 | interior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.87567 | 10.4822 | 272.816 | 0.05 | 426 | 730 | 990 | 1282
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.02 | 748 | 1173 | 1516 | 1887
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.025 | 672 | 1075 | 1403 | 1760
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.03 | 608 | 989 | 1302 | 1646
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.035 | 552 | 912 | 1211 | 1542
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.04 | 504 | 844 | 1130 | 1447
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.045 | 463 | 784 | 1056 | 1361
| 34 | 34 | interior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.87556 | 10.4816 | 272.816 | 0.05 | 426 | 730 | 990 | 1282
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.02 | 748 | 1173 | 1516 | 1887
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.025 | 672 | 1075 | 1403 | 1760
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.03 | 608 | 989 | 1302 | 1646
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.035 | 552 | 912 | 1211 | 1542
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.04 | 504 | 844 | 1130 | 1447
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.045 | 463 | 784 | 1056 | 1361
| 34 | 34 | interior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.87544 | 10.4809 | 272.816 | 0.05 | 426 | 730 | 990 | 1282
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.02 | 748 | 1173 | 1516 | 1887
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.025 | 672 | 1075 | 1403 | 1760
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.03 | 608 | 989 | 1302 | 1646
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.035 | 552 | 912 | 1211 | 1542
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.04 | 504 | 844 | 1130 | 1447
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.045 | 463 | 784 | 1056 | 1361
| 34 | 34 | interior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.87534 | 10.4803 | 272.816 | 0.05 | 426 | 730 | 990 | 1282

## exterior_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.03 | 3434 | 12160 | 12578 | 13010
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.035 | 3304 | 10423 | 10781 | 11151
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.04 | 3181 | 9120 | 9433 | 9758
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.045 | 3064 | 8106 | 8385 | 8673
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.05 | 2954 | 7296 | 7547 | 7806
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.055 | 2848 | 6633 | 6861 | 7096
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.06 | 2749 | 6080 | 6289 | 6505
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.065 | 2654 | 5612 | 5805 | 6005
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00406 | 0.00336 | 0.00698 | 0.00269 | 0.00201 | 0.00225 | 0.00271 | 0.00645 | 0.00645 | 0.00201 | 0.00209 | 0.00209 | 0.25549 | 3.376 | 186.116 | 0.07 | 2564 | 5211 | 5390 | 5576
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.03 | 3021 | 10946 | 11372 | 11815
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.035 | 2894 | 9382 | 9747 | 10127
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.04 | 2774 | 8209 | 8529 | 8861
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.045 | 2661 | 7297 | 7581 | 7876
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.05 | 2555 | 6567 | 6823 | 7089
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.055 | 2455 | 5970 | 6203 | 6444
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.06 | 2360 | 5473 | 5686 | 5907
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.065 | 2270 | 5052 | 5249 | 5453
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00402 | 0.00333 | 0.0069 | 0.00266 | 0.00201 | 0.00223 | 0.00268 | 0.00638 | 0.00638 | 0.00201 | 0.00207 | 0.00207 | 0.2675 | 3.8181 | 186.116 | 0.07 | 2186 | 4691 | 4874 | 5063
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.03 | 2939 | 10698 | 11125 | 11570
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.035 | 2813 | 9169 | 9536 | 9917
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.04 | 2694 | 8023 | 8344 | 8677
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.045 | 2582 | 7132 | 7417 | 7713
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.05 | 2476 | 6419 | 6675 | 6942
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.055 | 2377 | 5835 | 6068 | 6311
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.06 | 2284 | 5349 | 5563 | 5785
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.065 | 2195 | 4937 | 5135 | 5340
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.07 | 2112 | 4585 | 4768 | 4959
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.03 | 2846 | 10412 | 10841 | 11288
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.035 | 2720 | 8924 | 9292 | 9675
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.04 | 2602 | 7809 | 8131 | 8466
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.045 | 2491 | 6941 | 7227 | 7525
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.05 | 2387 | 6247 | 6505 | 6773
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.055 | 2289 | 5679 | 5913 | 6157
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.06 | 2197 | 5206 | 5421 | 5644
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.065 | 2110 | 4805 | 5004 | 5210
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00394 | 0.00326 | 0.00675 | 0.0026 | 0.00201 | 0.00218 | 0.00262 | 0.00624 | 0.00624 | 0.00201 | 0.00202 | 0.00202 | 0.29885 | 4.0357 | 186.116 | 0.07 | 2028 | 4462 | 4646 | 4838
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.03 | 2729 | 10049 | 10481 | 10930
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.035 | 2605 | 8614 | 8983 | 9369
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.04 | 2488 | 7537 | 7860 | 8198
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.045 | 2378 | 6700 | 6987 | 7287
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.05 | 2276 | 6030 | 6288 | 6558
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.055 | 2179 | 5482 | 5717 | 5962
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.06 | 2089 | 5025 | 5240 | 5465
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.065 | 2004 | 4638 | 4837 | 5045
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00389 | 0.00322 | 0.00668 | 0.00257 | 0.00201 | 0.00216 | 0.00259 | 0.00617 | 0.00617 | 0.00201 | 0.00201 | 0.00201 | 0.32305 | 4.1959 | 186.116 | 0.07 | 1924 | 4307 | 4492 | 4684
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.03 | 2069 | 7825 | 8230 | 8655
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.035 | 1959 | 6707 | 7054 | 7419
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.04 | 1857 | 5869 | 6172 | 6491
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.045 | 1763 | 5217 | 5486 | 5770
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.05 | 1675 | 4695 | 4938 | 5193
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.055 | 1594 | 4268 | 4489 | 4721
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.06 | 1518 | 3913 | 4115 | 4327
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.065 | 1448 | 3612 | 3798 | 3995
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00355 | 0.00295 | 0.00608 | 0.00235 | 0.00199 | 0.00199 | 0.00237 | 0.00563 | 0.00563 | 0.00199 | 0.00199 | 0.00199 | 0.48224 | 5.038 | 200.566 | 0.07 | 1383 | 3354 | 3527 | 3709
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.03 | 1841 | 7046 | 7450 | 7878
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.035 | 1735 | 6039 | 6386 | 6752
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.04 | 1637 | 5284 | 5588 | 5908
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.045 | 1547 | 4697 | 4967 | 5252
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.05 | 1464 | 4228 | 4470 | 4727
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.055 | 1388 | 3843 | 4064 | 4297
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.06 | 1317 | 3523 | 3725 | 3939
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.065 | 1252 | 3252 | 3439 | 3636
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00351 | 0.00292 | 0.00601 | 0.00233 | 0.00199 | 0.00199 | 0.00235 | 0.00557 | 0.00557 | 0.00199 | 0.00199 | 0.00199 | 0.48448 | 5.5813 | 200.566 | 0.07 | 1192 | 3020 | 3193 | 3376
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.03 | 1833 | 7019 | 7423 | 7851
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.035 | 1727 | 6016 | 6363 | 6729
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.04 | 1629 | 5264 | 5568 | 5888
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.045 | 1540 | 4679 | 4949 | 5234
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.05 | 1457 | 4212 | 4454 | 4711
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.055 | 1381 | 3829 | 4049 | 4282
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.06 | 1311 | 3510 | 3712 | 3926
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.065 | 1246 | 3240 | 3426 | 3624
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.07 | 1186 | 3008 | 3181 | 3365
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.03 | 1830 | 7006 | 7410 | 7838
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.035 | 1723 | 6005 | 6352 | 6718
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.04 | 1626 | 5254 | 5558 | 5878
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.045 | 1536 | 4671 | 4940 | 5225
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.05 | 1454 | 4204 | 4446 | 4703
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.055 | 1378 | 3821 | 4042 | 4275
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.06 | 1307 | 3503 | 3705 | 3919
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.065 | 1243 | 3234 | 3420 | 3617
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00343 | 0.00286 | 0.00589 | 0.00228 | 0.00199 | 0.00199 | 0.0023 | 0.00545 | 0.00545 | 0.00199 | 0.00199 | 0.00199 | 0.49026 | 5.6145 | 200.566 | 0.07 | 1183 | 3003 | 3176 | 3359
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.03 | 1818 | 6966 | 7371 | 7798
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.035 | 1712 | 5971 | 6318 | 6684
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.04 | 1615 | 5225 | 5528 | 5849
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.045 | 1525 | 4644 | 4914 | 5199
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.05 | 1443 | 4180 | 4422 | 4679
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.055 | 1367 | 3800 | 4020 | 4254
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.06 | 1298 | 3483 | 3685 | 3899
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.065 | 1233 | 3215 | 3402 | 3599
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0034 | 0.00282 | 0.00582 | 0.00225 | 0.00199 | 0.00199 | 0.00227 | 0.00539 | 0.00539 | 0.00199 | 0.00199 | 0.00199 | 0.49422 | 5.6371 | 200.566 | 0.07 | 1174 | 2986 | 3159 | 3342
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.03 | 1659 | 6367 | 6744 | 7143
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.035 | 1560 | 5457 | 5780 | 6122
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.04 | 1470 | 4775 | 5058 | 5357
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.045 | 1388 | 4245 | 4496 | 4762
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.05 | 1312 | 3820 | 4046 | 4286
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.055 | 1242 | 3473 | 3678 | 3896
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.06 | 1178 | 3183 | 3372 | 3571
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.065 | 1119 | 2939 | 3112 | 3297
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00314 | 0.00262 | 0.00538 | 0.00209 | 0.00198 | 0.00198 | 0.00211 | 0.00499 | 0.00499 | 0.00198 | 0.00198 | 0.00198 | 0.53869 | 5.7474 | 215.016 | 0.07 | 1064 | 2729 | 2890 | 3061
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.03 | 1444 | 5085 | 5968 | 6367
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.035 | 1350 | 4390 | 5116 | 5457
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.04 | 1265 | 3865 | 4476 | 4775
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.045 | 1188 | 3455 | 3979 | 4245
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.05 | 1117 | 3123 | 3581 | 3820
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.055 | 1053 | 2850 | 3256 | 3473
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.06 | 995 | 2621 | 2984 | 3183
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.065 | 941 | 2426 | 2755 | 2939
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00311 | 0.00259 | 0.00532 | 0.00206 | 0.00198 | 0.00198 | 0.00208 | 0.00494 | 0.00494 | 0.00198 | 0.00198 | 0.00198 | 0.55772 | 6.4636 | 215.016 | 0.07 | 892 | 2258 | 2558 | 2729
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.03 | 1402 | 4739 | 5812 | 6209
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.035 | 1309 | 4105 | 4981 | 5322
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.045 | 1149 | 3246 | 3874 | 4140
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.05 | 1080 | 2940 | 3487 | 3726
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.055 | 1017 | 2688 | 3170 | 3387
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.06 | 959 | 2475 | 2906 | 3105
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.065 | 907 | 2294 | 2682 | 2866
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.07 | 859 | 2137 | 2491 | 2661
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.03 | 1402 | 4739 | 5812 | 6209
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.035 | 1309 | 4105 | 4981 | 5322
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.045 | 1149 | 3246 | 3874 | 4140
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.05 | 1080 | 2940 | 3487 | 3726
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.055 | 1017 | 2688 | 3170 | 3387
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.06 | 959 | 2475 | 2906 | 3105
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.065 | 907 | 2294 | 2682 | 2866
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00305 | 0.00253 | 0.00521 | 0.00202 | 0.00198 | 0.00198 | 0.00204 | 0.00483 | 0.00483 | 0.00198 | 0.00198 | 0.00198 | 0.58443 | 6.6166 | 215.016 | 0.07 | 859 | 2137 | 2491 | 2661
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.03 | 1402 | 4739 | 5812 | 6209
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.035 | 1309 | 4105 | 4981 | 5322
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.045 | 1149 | 3246 | 3874 | 4140
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.05 | 1080 | 2940 | 3487 | 3726
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.055 | 1017 | 2688 | 3170 | 3387
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.06 | 959 | 2475 | 2906 | 3105
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.065 | 907 | 2294 | 2682 | 2866
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00301 | 0.00251 | 0.00516 | 0.002 | 0.00198 | 0.00198 | 0.00202 | 0.00478 | 0.00478 | 0.00198 | 0.00198 | 0.00198 | 0.58422 | 6.6154 | 215.016 | 0.07 | 859 | 2137 | 2491 | 2661
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.03 | 1363 | 4844 | 5629 | 6002
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.035 | 1275 | 4179 | 4825 | 5145
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.04 | 1195 | 3678 | 4222 | 4502
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.045 | 1122 | 3285 | 3753 | 4001
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.05 | 1056 | 2968 | 3377 | 3601
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.055 | 996 | 2708 | 3070 | 3274
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.06 | 940 | 2489 | 2814 | 3001
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.065 | 890 | 2303 | 2598 | 2770
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00282 | 0.00235 | 0.00482 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00446 | 0.00446 | 0.00196 | 0.00196 | 0.00196 | 0.58395 | 6.4241 | 229.466 | 0.07 | 843 | 2144 | 2412 | 2572
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.035 | 1121 | 3043 | 4254 | 4633
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.045 | 977 | 2456 | 3318 | 3604
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.05 | 915 | 2242 | 2989 | 3243
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.055 | 860 | 2063 | 2720 | 2948
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.06 | 809 | 1910 | 2495 | 2703
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.065 | 763 | 1778 | 2305 | 2495
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00279 | 0.00232 | 0.00477 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00441 | 0.00441 | 0.00196 | 0.00196 | 0.00196 | 0.58382 | 7.0995 | 229.466 | 0.07 | 721 | 1663 | 2142 | 2317
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.035 | 1121 | 3043 | 4254 | 4633
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.045 | 977 | 2456 | 3318 | 3604
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.05 | 915 | 2242 | 2989 | 3243
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.055 | 860 | 2063 | 2720 | 2948
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.06 | 809 | 1910 | 2495 | 2703
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.065 | 763 | 1778 | 2305 | 2495
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.07 | 721 | 1663 | 2142 | 2317
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.035 | 1121 | 3043 | 4254 | 4633
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.045 | 977 | 2456 | 3318 | 3604
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.05 | 915 | 2242 | 2989 | 3243
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.055 | 860 | 2063 | 2720 | 2948
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.06 | 809 | 1910 | 2495 | 2703
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.065 | 763 | 1778 | 2305 | 2495
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00273 | 0.00227 | 0.00466 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00432 | 0.00432 | 0.00196 | 0.00196 | 0.00196 | 0.58376 | 7.0991 | 229.466 | 0.07 | 721 | 1663 | 2142 | 2317
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.035 | 1121 | 3043 | 4254 | 4633
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.045 | 977 | 2456 | 3318 | 3604
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.05 | 915 | 2242 | 2989 | 3243
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.055 | 860 | 2063 | 2720 | 2948
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.06 | 809 | 1910 | 2495 | 2703
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.065 | 763 | 1778 | 2305 | 2495
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00271 | 0.00225 | 0.00461 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00427 | 0.00427 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.07 | 721 | 1663 | 2142 | 2317
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.03 | 1181 | 3701 | 4917 | 5267
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.035 | 1101 | 3226 | 4215 | 4514
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.04 | 1028 | 2862 | 3688 | 3950
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.045 | 962 | 2575 | 3278 | 3511
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.05 | 903 | 2341 | 2950 | 3160
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.055 | 849 | 2146 | 2682 | 2873
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.06 | 800 | 1981 | 2459 | 2633
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.065 | 755 | 1840 | 2269 | 2431
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00255 | 0.00212 | 0.00435 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00403 | 0.00403 | 0.00195 | 0.00195 | 0.00195 | 0.58424 | 6.866 | 243.916 | 0.07 | 715 | 1718 | 2107 | 2257
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.055 | 732 | 1503 | 2234 | 2580
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.06 | 687 | 1404 | 2059 | 2365
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.065 | 647 | 1316 | 1909 | 2183
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00253 | 0.0021 | 0.0043 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00398 | 0.00398 | 0.00195 | 0.00195 | 0.00195 | 0.58439 | 7.5896 | 243.916 | 0.07 | 610 | 1239 | 1780 | 2027
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.055 | 732 | 1503 | 2234 | 2580
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.06 | 687 | 1404 | 2059 | 2365
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.065 | 647 | 1316 | 1909 | 2183
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.07 | 610 | 1239 | 1780 | 2027
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.055 | 732 | 1503 | 2234 | 2580
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.06 | 687 | 1404 | 2059 | 2365
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.065 | 647 | 1316 | 1909 | 2183
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00247 | 0.00205 | 0.00421 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.0039 | 0.0039 | 0.00195 | 0.00195 | 0.00195 | 0.58477 | 7.5921 | 243.916 | 0.07 | 610 | 1239 | 1780 | 2027
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.055 | 732 | 1503 | 2234 | 2580
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.06 | 687 | 1404 | 2059 | 2365
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.065 | 647 | 1316 | 1909 | 2183
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00245 | 0.00203 | 0.00416 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00386 | 0.00386 | 0.00195 | 0.00195 | 0.00195 | 0.58504 | 7.5939 | 243.916 | 0.07 | 610 | 1239 | 1780 | 2027
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.03 | 1030 | 2684 | 4082 | 4646
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.035 | 957 | 2377 | 3520 | 3982
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.04 | 891 | 2137 | 3096 | 3484
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.045 | 831 | 1943 | 2765 | 3097
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.05 | 778 | 1782 | 2498 | 2787
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.055 | 730 | 1646 | 2278 | 2534
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.06 | 686 | 1530 | 2094 | 2323
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.065 | 646 | 1428 | 1937 | 2144
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00366 | 0.00366 | 0.00194 | 0.00194 | 0.00194 | 0.58655 | 7.3207 | 258.366 | 0.07 | 610 | 1339 | 1803 | 1991
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.03 | 906 | 1439 | 2955 | 4090
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.035 | 836 | 1347 | 2606 | 3513
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.04 | 774 | 1263 | 2336 | 3079
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.045 | 719 | 1187 | 2119 | 2742
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.05 | 670 | 1118 | 1939 | 2471
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.055 | 626 | 1055 | 1788 | 2249
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.06 | 586 | 997 | 1659 | 2063
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.065 | 551 | 943 | 1547 | 1906
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0023 | 0.00194 | 0.00392 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00362 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.58715 | 8.0954 | 258.366 | 0.07 | 519 | 895 | 1450 | 1772
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.03 | 906 | 1439 | 2955 | 4090
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.035 | 836 | 1347 | 2606 | 3513
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.04 | 774 | 1263 | 2336 | 3079
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.045 | 719 | 1187 | 2119 | 2742
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.05 | 670 | 1118 | 1939 | 2471
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.055 | 626 | 1055 | 1788 | 2249
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.06 | 586 | 997 | 1659 | 2063
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.065 | 551 | 943 | 1547 | 1906
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.07 | 519 | 895 | 1450 | 1772
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.03 | 904 | 1437 | 2940 | 4079
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.035 | 835 | 1345 | 2594 | 3503
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.04 | 773 | 1261 | 2326 | 3072
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.045 | 718 | 1185 | 2110 | 2736
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.05 | 669 | 1116 | 1932 | 2466
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.055 | 625 | 1053 | 1782 | 2245
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.06 | 585 | 995 | 1653 | 2059
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.065 | 550 | 942 | 1542 | 1903
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00226 | 0.00194 | 0.00383 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00354 | 0.00354 | 0.00194 | 0.00194 | 0.00194 | 0.58859 | 8.1054 | 258.366 | 0.07 | 518 | 893 | 1445 | 1769
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.03 | 904 | 1437 | 2940 | 4079
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.035 | 835 | 1345 | 2594 | 3503
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.04 | 773 | 1261 | 2326 | 3072
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.045 | 718 | 1185 | 2110 | 2736
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.05 | 669 | 1116 | 1932 | 2466
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.055 | 625 | 1053 | 1782 | 2245
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.06 | 585 | 995 | 1653 | 2059
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.065 | 550 | 942 | 1542 | 1903
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00379 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58945 | 8.1113 | 258.366 | 0.07 | 518 | 893 | 1445 | 1769
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.03 | 901 | 1725 | 3209 | 4102
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.035 | 833 | 1577 | 2802 | 3516
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.04 | 773 | 1454 | 2489 | 3077
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.045 | 719 | 1349 | 2242 | 2735
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.05 | 671 | 1257 | 2040 | 2461
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.055 | 628 | 1177 | 1872 | 2238
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.06 | 589 | 1104 | 1730 | 2051
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.065 | 554 | 1040 | 1608 | 1893
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00214 | 0.00193 | 0.00362 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00336 | 0.00336 | 0.00193 | 0.00193 | 0.00193 | 0.59266 | 7.8023 | 272.816 | 0.07 | 522 | 983 | 1502 | 1758
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.03 | 790 | 1262 | 2073 | 3279
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.035 | 727 | 1177 | 1880 | 2855
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.04 | 671 | 1101 | 1723 | 2532
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.045 | 621 | 1032 | 1590 | 2277
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.05 | 577 | 969 | 1477 | 2069
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.055 | 538 | 911 | 1378 | 1896
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.06 | 503 | 859 | 1291 | 1751
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.065 | 471 | 812 | 1214 | 1626
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00211 | 0.00193 | 0.00358 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00332 | 0.00332 | 0.00193 | 0.00193 | 0.00193 | 0.59388 | 8.6324 | 272.816 | 0.07 | 443 | 769 | 1146 | 1518
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.03 | 789 | 1260 | 2059 | 3267
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.035 | 725 | 1176 | 1869 | 2846
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.04 | 669 | 1099 | 1713 | 2525
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.045 | 620 | 1030 | 1583 | 2271
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.05 | 576 | 967 | 1470 | 2064
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.055 | 537 | 910 | 1372 | 1892
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.06 | 502 | 858 | 1286 | 1747
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.065 | 470 | 811 | 1210 | 1623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.07 | 442 | 767 | 1141 | 1515
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.03 | 788 | 1259 | 2045 | 3256
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.035 | 724 | 1174 | 1858 | 2838
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.04 | 668 | 1098 | 1704 | 2518
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.045 | 619 | 1028 | 1575 | 2265
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.05 | 575 | 965 | 1463 | 2059
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.055 | 536 | 908 | 1366 | 1888
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.06 | 501 | 856 | 1281 | 1743
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.065 | 469 | 809 | 1205 | 1620
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00207 | 0.00193 | 0.00351 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00325 | 0.00325 | 0.00193 | 0.00193 | 0.00193 | 0.59684 | 8.6539 | 272.816 | 0.07 | 441 | 766 | 1137 | 1512
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.03 | 785 | 1255 | 2018 | 3234
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.035 | 722 | 1171 | 1835 | 2820
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.04 | 666 | 1094 | 1686 | 2503
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.045 | 617 | 1025 | 1559 | 2253
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.05 | 573 | 962 | 1450 | 2049
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.055 | 534 | 905 | 1354 | 1879
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.06 | 499 | 854 | 1270 | 1736
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.065 | 468 | 806 | 1195 | 1613
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00205 | 0.00193 | 0.00347 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00322 | 0.00322 | 0.00193 | 0.00193 | 0.00193 | 0.59857 | 8.6664 | 272.816 | 0.07 | 440 | 763 | 1129 | 1506

## 50%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.03 | 3207 | 11498 | 11921 | 12359
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.035 | 3078 | 9856 | 10218 | 10594
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.04 | 2957 | 8624 | 8941 | 9269
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.045 | 2842 | 7666 | 7947 | 8240
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.05 | 2734 | 6899 | 7153 | 7416
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.055 | 2631 | 6272 | 6502 | 6741
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.06 | 2534 | 5749 | 5961 | 6180
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.065 | 2442 | 5307 | 5502 | 5704
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00269 | 0.00201 | 0.00225 | 0.00407 | 0.00967 | 0.00967 | 0.00201 | 0.00209 | 0.00209 | 0.29133 | 3.6051 | 186.116 | 0.07 | 2355 | 4928 | 5109 | 5297
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.03 | 2824 | 10342 | 10772 | 11219
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.035 | 2698 | 8865 | 9233 | 9617
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.04 | 2580 | 7757 | 8079 | 8414
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.045 | 2469 | 6895 | 7181 | 7480
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.05 | 2366 | 6205 | 6463 | 6732
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.055 | 2268 | 5641 | 5876 | 6120
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.06 | 2176 | 5171 | 5386 | 5610
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.065 | 2090 | 4773 | 4972 | 5178
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00266 | 0.00201 | 0.00223 | 0.00402 | 0.00957 | 0.00957 | 0.00201 | 0.00207 | 0.00207 | 0.30328 | 4.0655 | 186.116 | 0.07 | 2008 | 4432 | 4617 | 4808
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.03 | 2758 | 10138 | 10569 | 11018
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.035 | 2633 | 8690 | 9059 | 9444
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.04 | 2516 | 7604 | 7927 | 8263
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.045 | 2406 | 6759 | 7046 | 7345
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.05 | 2303 | 6083 | 6341 | 6611
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.055 | 2206 | 5530 | 5765 | 6010
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.06 | 2115 | 5069 | 5284 | 5509
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.065 | 2030 | 4679 | 4878 | 5085
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00263 | 0.00201 | 0.00221 | 0.00398 | 0.00946 | 0.00946 | 0.00201 | 0.00205 | 0.00205 | 0.31707 | 4.1569 | 186.116 | 0.07 | 1950 | 4345 | 4529 | 4722
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.03 | 2681 | 9897 | 10329 | 10780
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.035 | 2557 | 8483 | 8853 | 9240
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.04 | 2440 | 7423 | 7747 | 8085
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.045 | 2331 | 6598 | 6886 | 7186
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.05 | 2230 | 5938 | 6197 | 6468
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.055 | 2134 | 5398 | 5634 | 5880
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.06 | 2044 | 4949 | 5164 | 5390
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.065 | 1960 | 4568 | 4767 | 4975
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0026 | 0.00201 | 0.00218 | 0.00393 | 0.00936 | 0.00936 | 0.00201 | 0.00202 | 0.00202 | 0.33423 | 4.2679 | 186.116 | 0.07 | 1881 | 4242 | 4427 | 4620
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.03 | 2582 | 9583 | 10016 | 10469
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.035 | 2458 | 8214 | 8585 | 8973
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.04 | 2343 | 7187 | 7512 | 7852
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.045 | 2236 | 6389 | 6677 | 6979
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.05 | 2136 | 5750 | 6010 | 6281
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.055 | 2042 | 5227 | 5463 | 5710
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.06 | 1954 | 4791 | 5008 | 5234
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.065 | 1871 | 4423 | 4623 | 4832
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00257 | 0.00201 | 0.00216 | 0.00388 | 0.00925 | 0.00925 | 0.00201 | 0.00201 | 0.00201 | 0.35822 | 4.4184 | 186.116 | 0.07 | 1794 | 4107 | 4293 | 4487
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.03 | 1988 | 7552 | 7956 | 8383
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.035 | 1879 | 6473 | 6820 | 7185
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.04 | 1779 | 5664 | 5967 | 6287
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.045 | 1686 | 5035 | 5304 | 5589
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.05 | 1600 | 4531 | 4774 | 5030
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.055 | 1520 | 4119 | 4340 | 4572
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.06 | 1447 | 3776 | 3978 | 4191
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.065 | 1378 | 3485 | 3672 | 3869
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00235 | 0.00199 | 0.00199 | 0.00356 | 0.00844 | 0.00844 | 0.00199 | 0.00199 | 0.00199 | 0.51677 | 5.2153 | 200.566 | 0.07 | 1315 | 3236 | 3410 | 3593
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.03 | 1767 | 6786 | 7190 | 7617
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.035 | 1662 | 5816 | 6162 | 6529
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.04 | 1565 | 5089 | 5392 | 5713
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.045 | 1477 | 4524 | 4793 | 5078
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.05 | 1396 | 4071 | 4314 | 4570
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.055 | 1322 | 3701 | 3922 | 4155
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.06 | 1253 | 3393 | 3595 | 3809
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.065 | 1190 | 3132 | 3318 | 3516
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00233 | 0.00199 | 0.00199 | 0.00353 | 0.00836 | 0.00836 | 0.00199 | 0.00199 | 0.00199 | 0.51883 | 5.7757 | 200.566 | 0.07 | 1131 | 2908 | 3081 | 3265
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.03 | 1763 | 6773 | 7177 | 7605
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.035 | 1658 | 5806 | 6152 | 6518
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.04 | 1562 | 5080 | 5383 | 5704
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.045 | 1474 | 4515 | 4785 | 5070
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.05 | 1393 | 4064 | 4306 | 4563
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.055 | 1318 | 3694 | 3915 | 4148
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.06 | 1250 | 3387 | 3588 | 3802
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.065 | 1187 | 3126 | 3312 | 3510
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.0023 | 0.00199 | 0.00199 | 0.00348 | 0.00826 | 0.00826 | 0.00199 | 0.00199 | 0.00199 | 0.52137 | 5.7899 | 200.566 | 0.07 | 1129 | 2903 | 3076 | 3259
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.03 | 1756 | 6748 | 7152 | 7579
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.035 | 1651 | 5784 | 6130 | 6497
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.04 | 1555 | 5061 | 5364 | 5685
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.045 | 1467 | 4499 | 4768 | 5053
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.05 | 1386 | 4049 | 4291 | 4548
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.055 | 1312 | 3681 | 3901 | 4134
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.06 | 1244 | 3374 | 3576 | 3790
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.065 | 1181 | 3114 | 3301 | 3498
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00228 | 0.00199 | 0.00199 | 0.00345 | 0.00817 | 0.00817 | 0.00199 | 0.00199 | 0.00199 | 0.52427 | 5.8059 | 200.566 | 0.07 | 1123 | 2892 | 3065 | 3248
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.03 | 1749 | 6723 | 7127 | 7554
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.035 | 1644 | 5763 | 6108 | 6475
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.04 | 1548 | 5042 | 5345 | 5666
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.045 | 1461 | 4482 | 4751 | 5036
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.05 | 1380 | 4034 | 4276 | 4533
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.055 | 1306 | 3667 | 3887 | 4121
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.06 | 1238 | 3361 | 3563 | 3777
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.065 | 1175 | 3103 | 3289 | 3487
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00225 | 0.00199 | 0.00199 | 0.00341 | 0.00809 | 0.00809 | 0.00199 | 0.00199 | 0.00199 | 0.52819 | 5.8276 | 200.566 | 0.07 | 1117 | 2881 | 3054 | 3238
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.03 | 1603 | 6169 | 6545 | 6944
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.035 | 1506 | 5288 | 5610 | 5952
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.04 | 1417 | 4627 | 4909 | 5208
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.045 | 1335 | 4113 | 4363 | 4630
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.05 | 1261 | 3701 | 3927 | 4167
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.055 | 1192 | 3365 | 3570 | 3788
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.06 | 1130 | 3085 | 3273 | 3472
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.065 | 1072 | 2847 | 3021 | 3205
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00209 | 0.00198 | 0.00198 | 0.00317 | 0.00749 | 0.00749 | 0.00198 | 0.00198 | 0.00198 | 0.57216 | 5.9233 | 215.016 | 0.07 | 1018 | 2644 | 2805 | 2976
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.03 | 1394 | 4674 | 5783 | 6180
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.035 | 1302 | 4051 | 4957 | 5298
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.04 | 1218 | 3579 | 4337 | 4635
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.045 | 1142 | 3207 | 3855 | 4120
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.05 | 1073 | 2906 | 3470 | 3708
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.055 | 1010 | 2658 | 3154 | 3371
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.06 | 953 | 2448 | 2891 | 3090
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.065 | 901 | 2269 | 2669 | 2853
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00206 | 0.00198 | 0.00198 | 0.00312 | 0.00741 | 0.00741 | 0.00198 | 0.00198 | 0.00198 | 0.59108 | 6.6541 | 215.016 | 0.07 | 853 | 2115 | 2478 | 2649
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00204 | 0.00198 | 0.00198 | 0.00309 | 0.00732 | 0.00732 | 0.00198 | 0.00198 | 0.00198 | 0.61794 | 6.8036 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00202 | 0.00198 | 0.00198 | 0.00306 | 0.00725 | 0.00725 | 0.00198 | 0.00198 | 0.00198 | 0.61766 | 6.8021 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.002 | 0.00198 | 0.00198 | 0.00303 | 0.00717 | 0.00717 | 0.00198 | 0.00198 | 0.00198 | 0.6173 | 6.8001 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.03 | 1318 | 4480 | 5462 | 5835
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.035 | 1231 | 3879 | 4682 | 5002
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.04 | 1152 | 3424 | 4097 | 4376
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.045 | 1081 | 3066 | 3642 | 3890
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.05 | 1016 | 2776 | 3277 | 3501
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.055 | 957 | 2537 | 2980 | 3183
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.06 | 903 | 2336 | 2731 | 2918
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.065 | 853 | 2164 | 2521 | 2693
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00669 | 0.00669 | 0.00196 | 0.00196 | 0.00196 | 0.61689 | 6.6028 | 229.466 | 0.07 | 808 | 2017 | 2341 | 2501
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00661 | 0.00661 | 0.00196 | 0.00196 | 0.00196 | 0.61673 | 7.2968 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00656 | 0.00656 | 0.00196 | 0.00196 | 0.00196 | 0.61664 | 7.2963 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00648 | 0.00648 | 0.00196 | 0.00196 | 0.00196 | 0.61649 | 7.2954 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00196 | 0.00196 | 0.00196 | 0.00294 | 0.00641 | 0.00641 | 0.00196 | 0.00196 | 0.00196 | 0.61671 | 7.2967 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.03 | 1142 | 3339 | 4722 | 5117
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.035 | 1062 | 2927 | 4053 | 4386
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.04 | 991 | 2610 | 3549 | 3838
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.045 | 927 | 2357 | 3157 | 3411
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.05 | 868 | 2150 | 2843 | 3070
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.055 | 816 | 1976 | 2586 | 2791
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.06 | 768 | 1829 | 2372 | 2558
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.065 | 724 | 1702 | 2190 | 2362
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00605 | 0.00605 | 0.00195 | 0.00195 | 0.00195 | 0.61706 | 7.0562 | 243.916 | 0.07 | 685 | 1592 | 2034 | 2193
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00597 | 0.00597 | 0.00195 | 0.00195 | 0.00195 | 0.61738 | 7.801 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00591 | 0.00591 | 0.00195 | 0.00195 | 0.00195 | 0.61755 | 7.802 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00585 | 0.00585 | 0.00195 | 0.00195 | 0.00195 | 0.61764 | 7.8026 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.03 | 1006 | 1909 | 3574 | 4582
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.035 | 930 | 1749 | 3121 | 3927
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.04 | 863 | 1613 | 2774 | 3436
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.045 | 803 | 1497 | 2499 | 3055
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.05 | 749 | 1396 | 2274 | 2749
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.055 | 701 | 1307 | 2087 | 2499
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.06 | 658 | 1227 | 1929 | 2291
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.065 | 618 | 1156 | 1793 | 2115
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00195 | 0.00195 | 0.00195 | 0.00292 | 0.00579 | 0.00579 | 0.00195 | 0.00195 | 0.00195 | 0.61811 | 7.8055 | 243.916 | 0.07 | 583 | 1092 | 1675 | 1964
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.03 | 994 | 2306 | 3778 | 4504
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.035 | 922 | 2065 | 3274 | 3861
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.04 | 857 | 1874 | 2891 | 3378
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.045 | 799 | 1716 | 2591 | 3003
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.05 | 746 | 1583 | 2347 | 2702
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.055 | 699 | 1469 | 2146 | 2457
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.06 | 657 | 1371 | 1977 | 2252
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.065 | 618 | 1284 | 1832 | 2079
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00549 | 0.00549 | 0.00194 | 0.00194 | 0.00194 | 0.61996 | 7.5263 | 258.366 | 0.07 | 583 | 1207 | 1708 | 1930
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.03 | 875 | 1393 | 2637 | 3829
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.035 | 806 | 1302 | 2348 | 3306
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.04 | 746 | 1220 | 2121 | 2911
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.045 | 692 | 1145 | 1936 | 2602
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.05 | 644 | 1077 | 1781 | 2352
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.055 | 601 | 1015 | 1650 | 2147
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.06 | 562 | 958 | 1536 | 1974
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.065 | 528 | 906 | 1437 | 1828
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00543 | 0.00543 | 0.00194 | 0.00194 | 0.00194 | 0.62055 | 8.3225 | 258.366 | 0.07 | 497 | 859 | 1350 | 1702
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.03 | 874 | 1391 | 2622 | 3818
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.035 | 805 | 1300 | 2336 | 3296
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.04 | 744 | 1218 | 2111 | 2903
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.045 | 691 | 1143 | 1928 | 2595
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.05 | 643 | 1075 | 1774 | 2347
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.055 | 600 | 1013 | 1644 | 2142
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.06 | 561 | 956 | 1531 | 1970
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.065 | 527 | 905 | 1432 | 1824
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00537 | 0.00537 | 0.00194 | 0.00194 | 0.00194 | 0.62143 | 8.3284 | 258.366 | 0.07 | 496 | 857 | 1346 | 1699
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.03 | 872 | 1389 | 2608 | 3806
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.035 | 804 | 1298 | 2325 | 3287
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.04 | 743 | 1216 | 2102 | 2895
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.045 | 689 | 1141 | 1920 | 2589
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.05 | 641 | 1073 | 1767 | 2341
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.055 | 599 | 1011 | 1637 | 2138
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.06 | 560 | 955 | 1525 | 1966
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.065 | 526 | 903 | 1427 | 1820
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00531 | 0.00531 | 0.00194 | 0.00194 | 0.00194 | 0.62248 | 8.3354 | 258.366 | 0.07 | 495 | 855 | 1341 | 1695
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.03 | 872 | 1389 | 2608 | 3806
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.035 | 804 | 1298 | 2325 | 3287
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.04 | 743 | 1216 | 2102 | 2895
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.045 | 689 | 1141 | 1920 | 2589
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.05 | 641 | 1073 | 1767 | 2341
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.055 | 599 | 1011 | 1637 | 2138
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.06 | 560 | 955 | 1525 | 1966
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.065 | 526 | 903 | 1427 | 1820
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00194 | 0.00194 | 0.00194 | 0.00291 | 0.00525 | 0.00525 | 0.00194 | 0.00194 | 0.00194 | 0.62338 | 8.3415 | 258.366 | 0.07 | 495 | 855 | 1341 | 1695
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.03 | 868 | 1377 | 2894 | 3952
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.035 | 801 | 1290 | 2546 | 3390
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.04 | 742 | 1210 | 2277 | 2968
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.045 | 690 | 1138 | 2061 | 2640
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.05 | 643 | 1072 | 1884 | 2377
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.055 | 601 | 1011 | 1735 | 2161
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.06 | 563 | 956 | 1608 | 1981
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.065 | 529 | 905 | 1499 | 1830
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00504 | 0.00504 | 0.00193 | 0.00193 | 0.00193 | 0.6274 | 8.0277 | 272.816 | 0.07 | 498 | 859 | 1403 | 1699
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.03 | 761 | 1219 | 1730 | 2998
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.035 | 699 | 1135 | 1602 | 2632
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.04 | 644 | 1060 | 1492 | 2351
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.045 | 595 | 992 | 1394 | 2126
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.05 | 552 | 930 | 1307 | 1941
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.055 | 514 | 874 | 1229 | 1786
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.06 | 480 | 823 | 1159 | 1655
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.065 | 450 | 777 | 1096 | 1542
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00498 | 0.00498 | 0.00193 | 0.00193 | 0.00193 | 0.62866 | 8.8816 | 272.816 | 0.07 | 422 | 735 | 1038 | 1442
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.03 | 760 | 1217 | 1717 | 2987
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.035 | 697 | 1133 | 1591 | 2624
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.04 | 643 | 1058 | 1483 | 2343
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.045 | 594 | 990 | 1386 | 2120
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.05 | 551 | 929 | 1301 | 1936
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.055 | 513 | 873 | 1223 | 1782
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.06 | 479 | 822 | 1154 | 1651
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.065 | 449 | 776 | 1091 | 1538
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00493 | 0.00493 | 0.00193 | 0.00193 | 0.00193 | 0.63036 | 8.8936 | 272.816 | 0.07 | 422 | 734 | 1034 | 1439
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.03 | 758 | 1214 | 1689 | 2964
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.035 | 695 | 1130 | 1569 | 2606
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.04 | 641 | 1055 | 1464 | 2329
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.045 | 592 | 987 | 1371 | 2108
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.05 | 549 | 926 | 1287 | 1926
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.055 | 511 | 870 | 1212 | 1773
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.06 | 478 | 819 | 1144 | 1644
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.065 | 447 | 773 | 1082 | 1532
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00487 | 0.00487 | 0.00193 | 0.00193 | 0.00193 | 0.63231 | 8.9073 | 272.816 | 0.07 | 420 | 731 | 1026 | 1433
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.03 | 756 | 1212 | 1676 | 2953
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.035 | 694 | 1129 | 1558 | 2597
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.04 | 639 | 1053 | 1455 | 2322
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.045 | 591 | 985 | 1363 | 2102
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.05 | 548 | 924 | 1280 | 1921
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.055 | 511 | 868 | 1206 | 1769
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.06 | 477 | 818 | 1138 | 1640
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.065 | 446 | 772 | 1077 | 1528
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.00193 | 0.00193 | 0.00193 | 0.0029 | 0.00483 | 0.00483 | 0.00193 | 0.00193 | 0.00193 | 0.63444 | 8.9223 | 272.816 | 0.07 | 419 | 730 | 1021 | 1430

## 25%col_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.03 | 3312 | 11807 | 12227 | 12663
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.035 | 3183 | 10120 | 10481 | 10854
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.04 | 3061 | 8855 | 9171 | 9497
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.045 | 2945 | 7871 | 8152 | 8442
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.05 | 2835 | 7084 | 7336 | 7598
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.055 | 2731 | 6440 | 6669 | 6907
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.06 | 2633 | 5903 | 6114 | 6331
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.065 | 2540 | 5449 | 5643 | 5844
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00269 | 0.00201 | 0.00225 | 0.00339 | 0.00806 | 0.00806 | 0.00201 | 0.00209 | 0.00209 | 0.27392 | 3.4957 | 186.116 | 0.07 | 2451 | 5060 | 5240 | 5427
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.03 | 2916 | 10625 | 11053 | 11498
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.035 | 2789 | 9107 | 9474 | 9856
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.04 | 2670 | 7969 | 8290 | 8624
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.045 | 2559 | 7083 | 7369 | 7666 | f
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.05 | 2454 | 6375 | 6632 | 6899
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.055 | 2355 | 5795 | 6029 | 6272
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.06 | 2261 | 5312 | 5527 | 5749
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.065 | 2174 | 4904 | 5101 | 5307
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00266 | 0.00201 | 0.00223 | 0.00335 | 0.00797 | 0.00797 | 0.00201 | 0.00207 | 0.00207 | 0.28596 | 3.9477 | 186.116 | 0.07 | 2091 | 4554 | 4737 | 4928
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.03 | 2846 | 10412 | 10841 | 11288
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.035 | 2720 | 8924 | 9292 | 9675
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.04 | 2602 | 7809 | 8131 | 8466
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.045 | 2491 | 6941 | 7227 | 7525
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.05 | 2387 | 6247 | 6505 | 6773
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.055 | 2289 | 5679 | 5913 | 6157
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.06 | 2197 | 5206 | 5421 | 5644
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.065 | 2110 | 4805 | 5004 | 5210
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00263 | 0.00201 | 0.00221 | 0.00331 | 0.00789 | 0.00789 | 0.00201 | 0.00205 | 0.00205 | 0.29984 | 4.0423 | 186.116 | 0.07 | 2028 | 4462 | 4646 | 4838
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.03 | 2758 | 10138 | 10569 | 11018
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.035 | 2633 | 8690 | 9059 | 9444
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.04 | 2516 | 7604 | 7927 | 8263
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.045 | 2406 | 6759 | 7046 | 7345
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.05 | 2303 | 6083 | 6341 | 6611
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.055 | 2206 | 5530 | 5765 | 6010
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.06 | 2115 | 5069 | 5284 | 5509
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.065 | 2030 | 4679 | 4878 | 5085
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.0026 | 0.00201 | 0.00218 | 0.00328 | 0.0078 | 0.0078 | 0.00201 | 0.00202 | 0.00202 | 0.31707 | 4.1569 | 186.116 | 0.07 | 1950 | 4345 | 4529 | 4722
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.03 | 2654 | 9812 | 10244 | 10695
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.035 | 2530 | 8410 | 8781 | 9167
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.04 | 2414 | 7359 | 7683 | 8021
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.045 | 2305 | 6541 | 6829 | 7130
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.05 | 2204 | 5887 | 6146 | 6417
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.055 | 2109 | 5352 | 5588 | 5834
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.06 | 2020 | 4906 | 5122 | 5348
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.065 | 1936 | 4529 | 4728 | 4936
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00257 | 0.00201 | 0.00216 | 0.00324 | 0.00771 | 0.00771 | 0.00201 | 0.00201 | 0.00201 | 0.34115 | 4.3118 | 186.116 | 0.07 | 1857 | 4205 | 4390 | 4584
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.03 | 2028 | 7687 | 8091 | 8517
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.035 | 1918 | 6589 | 6935 | 7300
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.04 | 1817 | 5765 | 6068 | 6388
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.045 | 1723 | 5124 | 5394 | 5678
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.05 | 1637 | 4612 | 4855 | 5110
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.055 | 1556 | 4193 | 4413 | 4646
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.06 | 1482 | 3843 | 4046 | 4259
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.065 | 1413 | 3548 | 3734 | 3931
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00235 | 0.00199 | 0.00199 | 0.00296 | 0.00704 | 0.00704 | 0.00199 | 0.00199 | 0.00199 | 0.50004 | 5.1302 | 200.566 | 0.07 | 1348 | 3294 | 3468 | 3650
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.03 | 1803 | 6914 | 7318 | 7746
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.035 | 1698 | 5926 | 6273 | 6639
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.04 | 1600 | 5186 | 5489 | 5809
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.045 | 1511 | 4609 | 4879 | 5164
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.05 | 1429 | 4148 | 4391 | 4648
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.055 | 1354 | 3771 | 3992 | 4225
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.06 | 1285 | 3457 | 3659 | 3873
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.065 | 1220 | 3191 | 3378 | 3575
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00233 | 0.00199 | 0.00199 | 0.00294 | 0.00696 | 0.00696 | 0.00199 | 0.00199 | 0.00199 | 0.50218 | 5.6823 | 200.566 | 0.07 | 1161 | 2963 | 3136 | 3320
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.03 | 1796 | 6888 | 7292 | 7720
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.035 | 1690 | 5904 | 6250 | 6617
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.04 | 1593 | 5166 | 5469 | 5790
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.045 | 1504 | 4592 | 4861 | 5147
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.05 | 1423 | 4133 | 4375 | 4632
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.055 | 1347 | 3757 | 3978 | 4211
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.06 | 1278 | 3444 | 3646 | 3860
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.065 | 1214 | 3179 | 3366 | 3563
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.0023 | 0.00199 | 0.00199 | 0.0029 | 0.00689 | 0.00689 | 0.00199 | 0.00199 | 0.00199 | 0.5048 | 5.6971 | 200.566 | 0.07 | 1155 | 2952 | 3125 | 3309
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.03 | 1792 | 6875 | 7279 | 7707
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.035 | 1687 | 5893 | 6239 | 6606
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.04 | 1590 | 5156 | 5459 | 5780
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.045 | 1501 | 4583 | 4853 | 5138
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.05 | 1419 | 4125 | 4368 | 4624
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.055 | 1344 | 3750 | 3970 | 4204
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.06 | 1275 | 3438 | 3640 | 3853
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.065 | 1211 | 3173 | 3360 | 3557
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00228 | 0.00199 | 0.00199 | 0.00287 | 0.00681 | 0.00681 | 0.00199 | 0.00199 | 0.00199 | 0.50776 | 5.7138 | 200.566 | 0.07 | 1152 | 2947 | 3120 | 3303
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.03 | 1781 | 6837 | 7241 | 7668
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.035 | 1676 | 5860 | 6206 | 6573
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.04 | 1579 | 5128 | 5430 | 5751
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.045 | 1491 | 4558 | 4827 | 5112
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.05 | 1409 | 4102 | 4344 | 4601
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.055 | 1334 | 3729 | 3949 | 4183
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.06 | 1266 | 3418 | 3620 | 3834
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.065 | 1202 | 3155 | 3342 | 3539
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00225 | 0.00199 | 0.00199 | 0.00284 | 0.00674 | 0.00674 | 0.00199 | 0.00199 | 0.00199 | 0.51174 | 5.7362 | 200.566 | 0.07 | 1143 | 2930 | 3103 | 3286
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.03 | 1629 | 6261 | 6638 | 7037
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.035 | 1531 | 5367 | 5689 | 6031
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.04 | 1442 | 4696 | 4978 | 5278
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.045 | 1360 | 4174 | 4425 | 4691
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.05 | 1284 | 3757 | 3983 | 4222
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.055 | 1215 | 3415 | 3620 | 3838
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.06 | 1152 | 3131 | 3319 | 3518
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.065 | 1093 | 2890 | 3063 | 3248
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00209 | 0.00198 | 0.00198 | 0.00264 | 0.00624 | 0.00624 | 0.00198 | 0.00198 | 0.00198 | 0.55593 | 5.8386 | 215.016 | 0.07 | 1039 | 2683 | 2845 | 3016
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.03 | 1417 | 4869 | 5870 | 6268
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.035 | 1324 | 4212 | 5031 | 5372
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.045 | 1163 | 3324 | 3913 | 4178
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.05 | 1094 | 3009 | 3522 | 3761
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.055 | 1030 | 2749 | 3202 | 3419
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.06 | 972 | 2530 | 2935 | 3134
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.065 | 919 | 2344 | 2709 | 2893
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00206 | 0.00198 | 0.00198 | 0.0026 | 0.00618 | 0.00618 | 0.00198 | 0.00198 | 0.00198 | 0.57489 | 6.5623 | 215.016 | 0.07 | 871 | 2182 | 2516 | 2686
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00204 | 0.00198 | 0.00198 | 0.00258 | 0.0061 | 0.0061 | 0.00198 | 0.00198 | 0.00198 | 0.60179 | 6.7141 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00202 | 0.00198 | 0.00198 | 0.00255 | 0.00604 | 0.00604 | 0.00198 | 0.00198 | 0.00198 | 0.60155 | 6.7128 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.002 | 0.00198 | 0.00198 | 0.00253 | 0.00598 | 0.00598 | 0.00198 | 0.00198 | 0.00198 | 0.60125 | 6.7111 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.03 | 1338 | 4642 | 5536 | 5909
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.035 | 1250 | 4012 | 4745 | 5064
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.04 | 1171 | 3537 | 4152 | 4431
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.045 | 1099 | 3163 | 3690 | 3939
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.05 | 1033 | 2862 | 3321 | 3545
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.055 | 974 | 2613 | 3019 | 3223
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.06 | 919 | 2404 | 2768 | 2954
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.065 | 869 | 2226 | 2555 | 2727
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00558 | 0.00558 | 0.00196 | 0.00196 | 0.00196 | 0.60091 | 6.5167 | 229.466 | 0.07 | 824 | 2073 | 2372 | 2532
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00551 | 0.00551 | 0.00196 | 0.00196 | 0.00196 | 0.60078 | 7.2019 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00546 | 0.00546 | 0.00196 | 0.00196 | 0.00196 | 0.60071 | 7.2015 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.0054 | 0.0054 | 0.00196 | 0.00196 | 0.00196 | 0.60059 | 7.2007 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00196 | 0.00196 | 0.00196 | 0.00245 | 0.00534 | 0.00534 | 0.00196 | 0.00196 | 0.00196 | 0.6008 | 7.202 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.03 | 1162 | 3529 | 4846 | 5195
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.035 | 1082 | 3084 | 4153 | 4453
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.04 | 1010 | 2743 | 3634 | 3896
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.045 | 945 | 2471 | 3230 | 3463
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.05 | 886 | 2250 | 2907 | 3117
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.055 | 833 | 2066 | 2643 | 2834
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.06 | 784 | 1909 | 2423 | 2597
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.065 | 740 | 1775 | 2236 | 2398
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00504 | 0.00504 | 0.00195 | 0.00195 | 0.00195 | 0.60115 | 6.9646 | 243.916 | 0.07 | 700 | 1658 | 2077 | 2226
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00498 | 0.00498 | 0.00195 | 0.00195 | 0.00195 | 0.60145 | 7.6996 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00492 | 0.00492 | 0.00195 | 0.00195 | 0.00195 | 0.60162 | 7.7007 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00487 | 0.00487 | 0.00195 | 0.00195 | 0.00195 | 0.60171 | 7.7013 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00195 | 0.00195 | 0.00195 | 0.00244 | 0.00482 | 0.00482 | 0.00195 | 0.00195 | 0.00195 | 0.60214 | 7.704 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.03 | 1011 | 2486 | 3923 | 4571
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.035 | 938 | 2214 | 3391 | 3918
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.04 | 873 | 1999 | 2989 | 3428
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.045 | 814 | 1824 | 2674 | 3047
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.05 | 761 | 1678 | 2419 | 2742
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.055 | 714 | 1554 | 2209 | 2493
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.06 | 670 | 1446 | 2032 | 2285
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.065 | 631 | 1352 | 1882 | 2110
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00458 | 0.00458 | 0.00194 | 0.00194 | 0.00194 | 0.60385 | 7.4278 | 258.366 | 0.07 | 596 | 1270 | 1753 | 1959
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.03 | 890 | 1416 | 2796 | 3960
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.035 | 821 | 1324 | 2477 | 3409
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.04 | 760 | 1241 | 2228 | 2995
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.045 | 705 | 1166 | 2028 | 2672
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.05 | 657 | 1097 | 1860 | 2411
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.055 | 613 | 1034 | 1719 | 2198
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.06 | 574 | 977 | 1597 | 2019
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.065 | 539 | 925 | 1492 | 1867
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00452 | 0.00452 | 0.00194 | 0.00194 | 0.00194 | 0.60439 | 8.2134 | 258.366 | 0.07 | 507 | 876 | 1400 | 1737
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.03 | 889 | 1414 | 2781 | 3948
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.035 | 820 | 1322 | 2465 | 3400
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.04 | 759 | 1239 | 2218 | 2987
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.045 | 704 | 1164 | 2019 | 2666
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.05 | 655 | 1095 | 1853 | 2406
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.055 | 612 | 1033 | 1713 | 2194
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.06 | 573 | 975 | 1592 | 2015
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.065 | 538 | 923 | 1487 | 1863
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00447 | 0.00447 | 0.00194 | 0.00194 | 0.00194 | 0.60521 | 8.219 | 258.366 | 0.07 | 506 | 875 | 1395 | 1734
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.03 | 887 | 1412 | 2767 | 3936
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.035 | 818 | 1320 | 2453 | 3391
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.04 | 757 | 1237 | 2209 | 2980
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.045 | 703 | 1162 | 2011 | 2659
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.05 | 654 | 1093 | 1846 | 2401
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.055 | 611 | 1031 | 1707 | 2189
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.06 | 572 | 974 | 1586 | 2011
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.065 | 537 | 921 | 1482 | 1860
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00443 | 0.00443 | 0.00194 | 0.00194 | 0.00194 | 0.60617 | 8.2255 | 258.366 | 0.07 | 505 | 873 | 1391 | 1731
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.03 | 887 | 1412 | 2767 | 3936
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.035 | 818 | 1320 | 2453 | 3391
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.04 | 757 | 1237 | 2209 | 2980
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.045 | 703 | 1162 | 2011 | 2659
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.05 | 654 | 1093 | 1846 | 2401
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.055 | 611 | 1031 | 1707 | 2189
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.06 | 572 | 974 | 1586 | 2011
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.065 | 537 | 921 | 1482 | 1860
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00194 | 0.00194 | 0.00194 | 0.00242 | 0.00438 | 0.00438 | 0.00194 | 0.00194 | 0.00194 | 0.60701 | 8.2312 | 258.366 | 0.07 | 505 | 873 | 1391 | 1731
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.03 | 883 | 1520 | 3045 | 4032
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.035 | 816 | 1408 | 2668 | 3456
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.04 | 757 | 1311 | 2378 | 3024
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.045 | 704 | 1226 | 2148 | 2688
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.05 | 656 | 1149 | 1959 | 2419
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.055 | 614 | 1081 | 1801 | 2199
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.06 | 575 | 1018 | 1666 | 2016
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.065 | 541 | 962 | 1551 | 1861
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.0042 | 0.0042 | 0.00193 | 0.00193 | 0.00193 | 0.61071 | 7.9202 | 272.816 | 0.07 | 510 | 912 | 1450 | 1728
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.035 | 712 | 1155 | 1736 | 2739
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.04 | 656 | 1079 | 1603 | 2438
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.045 | 607 | 1011 | 1488 | 2199
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.05 | 564 | 948 | 1389 | 2003
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.055 | 525 | 892 | 1301 | 1839
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.06 | 491 | 840 | 1223 | 1701
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.065 | 460 | 794 | 1153 | 1582
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00415 | 0.00415 | 0.00193 | 0.00193 | 0.00193 | 0.61189 | 8.7623 | 272.816 | 0.07 | 432 | 751 | 1090 | 1478
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.03 | 774 | 1238 | 1881 | 3121
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.035 | 711 | 1153 | 1724 | 2731
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.04 | 655 | 1078 | 1593 | 2431
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.045 | 606 | 1009 | 1481 | 2193
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.05 | 563 | 947 | 1382 | 1998
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.055 | 524 | 890 | 1295 | 1835
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.06 | 490 | 839 | 1217 | 1697
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.065 | 459 | 792 | 1148 | 1579
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00411 | 0.00411 | 0.00193 | 0.00193 | 0.00193 | 0.61347 | 8.7737 | 272.816 | 0.07 | 431 | 750 | 1086 | 1475
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.03 | 771 | 1234 | 1853 | 3099
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.035 | 708 | 1150 | 1702 | 2713
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.04 | 653 | 1074 | 1575 | 2416
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.045 | 604 | 1006 | 1465 | 2180
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.05 | 561 | 944 | 1368 | 1988
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.055 | 522 | 887 | 1283 | 1826
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.06 | 488 | 836 | 1207 | 1690
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.065 | 457 | 789 | 1139 | 1572
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00406 | 0.00406 | 0.00193 | 0.00193 | 0.00193 | 0.61529 | 8.7867 | 272.816 | 0.07 | 430 | 747 | 1077 | 1469
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.03 | 770 | 1232 | 1840 | 3088
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.035 | 707 | 1148 | 1691 | 2704
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.04 | 652 | 1073 | 1566 | 2409
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.045 | 603 | 1004 | 1457 | 2174
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.05 | 560 | 942 | 1362 | 1982
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.055 | 521 | 886 | 1277 | 1822
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.06 | 487 | 835 | 1202 | 1686
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.065 | 456 | 788 | 1134 | 1569
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00193 | 0.00193 | 0.00193 | 0.00241 | 0.00402 | 0.00402 | 0.00193 | 0.00193 | 0.00193 | 0.61729 | 8.8009 | 272.816 | 0.07 | 429 | 746 | 1073 | 1466

## 25%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.03 | 3170 | 11390 | 11813 | 12252
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.035 | 3042 | 9762 | 10125 | 10502
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.04 | 2921 | 8542 | 8860 | 9189
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.045 | 2806 | 7593 | 7875 | 8168
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.05 | 2698 | 6834 | 7088 | 7351
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.055 | 2596 | 6212 | 6443 | 6683
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.06 | 2499 | 5695 | 5906 | 6126
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.065 | 2408 | 5257 | 5452 | 5655
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00508 | 0.0042 | 0.00873 | 0.00336 | 0.00251 | 0.00281 | 0.00339 | 0.00806 | 0.00806 | 0.00251 | 0.00261 | 0.00261 | 0.29809 | 3.6467 | 186.116 | 0.07 | 2321 | 4881 | 5063 | 5251
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.03 | 2794 | 10251 | 10681 | 11129
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.035 | 2669 | 8786 | 9155 | 9539
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.04 | 2551 | 7688 | 8011 | 8347
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.045 | 2441 | 6834 | 7121 | 7419
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.05 | 2337 | 6150 | 6408 | 6677
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.055 | 2240 | 5591 | 5826 | 6070
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.06 | 2149 | 5125 | 5340 | 5564
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.065 | 2063 | 4731 | 4930 | 5136
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00503 | 0.00416 | 0.00863 | 0.00333 | 0.00251 | 0.00279 | 0.00335 | 0.00797 | 0.00797 | 0.00251 | 0.00259 | 0.00259 | 0.31061 | 4.1143 | 186.116 | 0.07 | 1982 | 4393 | 4577 | 4770
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.03 | 2722 | 10027 | 10459 | 10908
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.035 | 2598 | 8595 | 8965 | 9350
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.04 | 2481 | 7521 | 7844 | 8181
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.045 | 2372 | 6685 | 6972 | 7272
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.05 | 2269 | 6016 | 6275 | 6545
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.055 | 2173 | 5470 | 5705 | 5950
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.06 | 2083 | 5014 | 5229 | 5454
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.065 | 1998 | 4628 | 4827 | 5035
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00411 | 0.00854 | 0.00329 | 0.00251 | 0.00276 | 0.00331 | 0.00789 | 0.00789 | 0.00251 | 0.00256 | 0.00256 | 0.32481 | 4.2073 | 186.116 | 0.07 | 1918 | 4297 | 4482 | 4675
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.03 | 2647 | 9791 | 10223 | 10674
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.035 | 2523 | 8392 | 8763 | 9149
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.04 | 2407 | 7343 | 7667 | 8006
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.045 | 2299 | 6527 | 6815 | 7116
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.05 | 2198 | 5874 | 6134 | 6405
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.055 | 2103 | 5340 | 5576 | 5822
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.06 | 2013 | 4895 | 5111 | 5337
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.065 | 1930 | 4519 | 4718 | 4927
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00407 | 0.00844 | 0.00325 | 0.00251 | 0.00272 | 0.00328 | 0.0078 | 0.0078 | 0.00251 | 0.00253 | 0.00253 | 0.34209 | 4.3178 | 186.116 | 0.07 | 1852 | 4196 | 4381 | 4575
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.03 | 2556 | 9502 | 9935 | 10388
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.035 | 2433 | 8144 | 8516 | 8904
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.04 | 2319 | 7126 | 7451 | 7791
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.045 | 2211 | 6335 | 6623 | 6926
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.05 | 2111 | 5701 | 5961 | 6233
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.055 | 2018 | 5183 | 5419 | 5666
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.06 | 1930 | 4751 | 4968 | 5194
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.065 | 1849 | 4385 | 4585 | 4795
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00486 | 0.00402 | 0.00835 | 0.00321 | 0.00251 | 0.0027 | 0.00324 | 0.00771 | 0.00771 | 0.00251 | 0.00251 | 0.00251 | 0.36564 | 4.4639 | 186.116 | 0.07 | 1772 | 4072 | 4258 | 4452
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.03 | 2010 | 7626 | 8031 | 8457
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.035 | 1901 | 6537 | 6884 | 7249
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.04 | 1800 | 5720 | 6023 | 6343
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.045 | 1707 | 5084 | 5354 | 5638
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.05 | 1620 | 4576 | 4819 | 5074
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.055 | 1540 | 4160 | 4380 | 4613
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.06 | 1466 | 3813 | 4015 | 4229
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.065 | 1397 | 3520 | 3707 | 3903
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00444 | 0.00369 | 0.0076 | 0.00294 | 0.00249 | 0.00249 | 0.00296 | 0.00704 | 0.00704 | 0.00249 | 0.00249 | 0.00249 | 0.50723 | 5.1669 | 200.566 | 0.07 | 1333 | 3268 | 3442 | 3624
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.03 | 1789 | 6862 | 7266 | 7694
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.035 | 1683 | 5882 | 6228 | 6595
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.04 | 1586 | 5147 | 5450 | 5771
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.045 | 1498 | 4575 | 4844 | 5129
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.05 | 1416 | 4117 | 4360 | 4616
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.055 | 1341 | 3743 | 3963 | 4197
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.06 | 1272 | 3431 | 3633 | 3847
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.065 | 1208 | 3167 | 3354 | 3551
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00439 | 0.00365 | 0.00751 | 0.00291 | 0.00249 | 0.00249 | 0.00294 | 0.00696 | 0.00696 | 0.00249 | 0.00249 | 0.00249 | 0.50957 | 5.724 | 200.566 | 0.07 | 1149 | 2941 | 3114 | 3297
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.03 | 1781 | 6837 | 7241 | 7668
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.035 | 1676 | 5860 | 6206 | 6573
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.04 | 1579 | 5128 | 5430 | 5751
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.045 | 1491 | 4558 | 4827 | 5112
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.05 | 1409 | 4102 | 4344 | 4601
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.055 | 1334 | 3729 | 3949 | 4183
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.06 | 1266 | 3418 | 3620 | 3834
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.065 | 1202 | 3155 | 3342 | 3539
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00434 | 0.00361 | 0.00744 | 0.00287 | 0.00249 | 0.00249 | 0.0029 | 0.00689 | 0.00689 | 0.00249 | 0.00249 | 0.00249 | 0.5124 | 5.7398 | 200.566 | 0.07 | 1143 | 2930 | 3103 | 3286
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.03 | 1774 | 6811 | 7215 | 7643
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.035 | 1669 | 5838 | 6184 | 6551
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.04 | 1572 | 5108 | 5411 | 5732
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.045 | 1484 | 4541 | 4810 | 5095
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.05 | 1403 | 4087 | 4329 | 4586
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.055 | 1328 | 3715 | 3935 | 4169
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.06 | 1259 | 3406 | 3608 | 3821
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.065 | 1196 | 3144 | 3330 | 3527
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00429 | 0.00358 | 0.00736 | 0.00285 | 0.00249 | 0.00249 | 0.00287 | 0.00681 | 0.00681 | 0.00249 | 0.00249 | 0.00249 | 0.51556 | 5.7575 | 200.566 | 0.07 | 1137 | 2919 | 3092 | 3275
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.03 | 1767 | 6786 | 7190 | 7617
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.035 | 1662 | 5816 | 6162 | 6529
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.04 | 1565 | 5089 | 5392 | 5713
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.045 | 1477 | 4524 | 4793 | 5078
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.05 | 1396 | 4071 | 4314 | 4570
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.055 | 1322 | 3701 | 3922 | 4155
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.06 | 1253 | 3393 | 3595 | 3809
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.065 | 1190 | 3132 | 3318 | 3516
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00425 | 0.00352 | 0.00728 | 0.00281 | 0.00249 | 0.00249 | 0.00284 | 0.00674 | 0.00674 | 0.00249 | 0.00249 | 0.00249 | 0.51974 | 5.7808 | 200.566 | 0.07 | 1131 | 2908 | 3081 | 3265
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.03 | 1619 | 6226 | 6603 | 7002
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.035 | 1521 | 5337 | 5659 | 6002
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.04 | 1432 | 4670 | 4952 | 5251
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.045 | 1350 | 4151 | 4402 | 4668
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.05 | 1276 | 3736 | 3962 | 4201
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.055 | 1207 | 3396 | 3601 | 3819
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.06 | 1143 | 3113 | 3301 | 3501
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.065 | 1085 | 2874 | 3047 | 3232
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00392 | 0.00328 | 0.00672 | 0.00261 | 0.00247 | 0.00247 | 0.00264 | 0.00624 | 0.00624 | 0.00247 | 0.00247 | 0.00247 | 0.56268 | 5.874 | 215.016 | 0.07 | 1032 | 2668 | 2830 | 3001
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.03 | 1410 | 4804 | 5841 | 6238
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.035 | 1317 | 4158 | 5006 | 5347
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.04 | 1232 | 3669 | 4380 | 4679
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.045 | 1156 | 3285 | 3894 | 4159
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.05 | 1087 | 2974 | 3504 | 3743
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.055 | 1023 | 2718 | 3186 | 3403
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.06 | 966 | 2502 | 2920 | 3119
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.065 | 913 | 2319 | 2696 | 2879
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00389 | 0.00324 | 0.00665 | 0.00258 | 0.00247 | 0.00247 | 0.0026 | 0.00618 | 0.00618 | 0.00247 | 0.00247 | 0.00247 | 0.57945 | 6.5883 | 215.016 | 0.07 | 865 | 2160 | 2503 | 2674
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00385 | 0.0032 | 0.00659 | 0.00255 | 0.00247 | 0.00247 | 0.00258 | 0.0061 | 0.0061 | 0.00247 | 0.00247 | 0.00247 | 0.60179 | 6.7141 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00381 | 0.00316 | 0.00651 | 0.00253 | 0.00247 | 0.00247 | 0.00255 | 0.00604 | 0.00604 | 0.00247 | 0.00247 | 0.00247 | 0.60155 | 6.7128 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.03 | 1379 | 4544 | 5726 | 6123
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.035 | 1287 | 3944 | 4908 | 5249
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.04 | 1203 | 3488 | 4294 | 4592
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.045 | 1128 | 3129 | 3817 | 4082
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.05 | 1059 | 2838 | 3436 | 3674
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.055 | 997 | 2597 | 3123 | 3340
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.06 | 940 | 2393 | 2863 | 3062
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.065 | 888 | 2220 | 2643 | 2826
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00376 | 0.00314 | 0.00645 | 0.0025 | 0.00247 | 0.00247 | 0.00253 | 0.00598 | 0.00598 | 0.00247 | 0.00247 | 0.00247 | 0.60125 | 6.7111 | 215.016 | 0.07 | 841 | 2069 | 2454 | 2624
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.03 | 1338 | 4642 | 5536 | 5909
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.035 | 1250 | 4012 | 4745 | 5064
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.04 | 1171 | 3537 | 4152 | 4431
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.045 | 1099 | 3163 | 3690 | 3939
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.05 | 1033 | 2862 | 3321 | 3545
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.055 | 974 | 2613 | 3019 | 3223
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.06 | 919 | 2404 | 2768 | 2954
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.065 | 869 | 2226 | 2555 | 2727
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00352 | 0.00294 | 0.00602 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00558 | 0.00558 | 0.00245 | 0.00245 | 0.00245 | 0.60091 | 6.5167 | 229.466 | 0.07 | 824 | 2073 | 2372 | 2532
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00349 | 0.0029 | 0.00596 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00551 | 0.00551 | 0.00245 | 0.00245 | 0.00245 | 0.60078 | 7.2019 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00345 | 0.00287 | 0.0059 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00546 | 0.00546 | 0.00245 | 0.00245 | 0.00245 | 0.60071 | 7.2015 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00341 | 0.00284 | 0.00582 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.0054 | 0.0054 | 0.00245 | 0.00245 | 0.00245 | 0.60059 | 7.2007 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.03 | 1184 | 3265 | 4792 | 5325
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.035 | 1101 | 2876 | 4122 | 4564
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.04 | 1026 | 2576 | 3617 | 3994
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.045 | 958 | 2334 | 3224 | 3550
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.05 | 897 | 2135 | 2909 | 3195
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.055 | 842 | 1968 | 2650 | 2905
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.06 | 792 | 1825 | 2432 | 2662
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.065 | 747 | 1700 | 2248 | 2458
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00339 | 0.00281 | 0.00576 | 0.00245 | 0.00245 | 0.00245 | 0.00245 | 0.00534 | 0.00534 | 0.00245 | 0.00245 | 0.00245 | 0.6008 | 7.202 | 229.466 | 0.07 | 705 | 1593 | 2091 | 2282
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.03 | 1162 | 3529 | 4846 | 5195
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.035 | 1082 | 3084 | 4153 | 4453
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.04 | 1010 | 2743 | 3634 | 3896
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.045 | 945 | 2471 | 3230 | 3463
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.05 | 886 | 2250 | 2907 | 3117
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.055 | 833 | 2066 | 2643 | 2834
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.06 | 784 | 1909 | 2423 | 2597
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.065 | 740 | 1775 | 2236 | 2398
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00319 | 0.00265 | 0.00544 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00504 | 0.00504 | 0.00244 | 0.00244 | 0.00244 | 0.60115 | 6.9646 | 243.916 | 0.07 | 700 | 1658 | 2077 | 2226
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00316 | 0.00263 | 0.00538 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00498 | 0.00498 | 0.00244 | 0.00244 | 0.00244 | 0.60145 | 7.6996 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00313 | 0.0026 | 0.00532 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00492 | 0.00492 | 0.00244 | 0.00244 | 0.00244 | 0.60162 | 7.7007 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00309 | 0.00256 | 0.00526 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00487 | 0.00487 | 0.00244 | 0.00244 | 0.00244 | 0.60171 | 7.7013 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.03 | 1024 | 2119 | 3742 | 4655
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.035 | 948 | 1921 | 3258 | 3990
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.04 | 880 | 1759 | 2888 | 3491
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.045 | 820 | 1623 | 2595 | 3103
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.05 | 765 | 1506 | 2358 | 2793
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.055 | 716 | 1405 | 2160 | 2539
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.06 | 672 | 1316 | 1994 | 2328
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.065 | 632 | 1236 | 1851 | 2149
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00306 | 0.00254 | 0.0052 | 0.00244 | 0.00244 | 0.00244 | 0.00244 | 0.00482 | 0.00482 | 0.00244 | 0.00244 | 0.00244 | 0.60214 | 7.704 | 243.916 | 0.07 | 596 | 1166 | 1727 | 1995
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.03 | 1011 | 2486 | 3923 | 4571
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.035 | 938 | 2214 | 3391 | 3918
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.04 | 873 | 1999 | 2989 | 3428
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.045 | 814 | 1824 | 2674 | 3047
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.05 | 761 | 1678 | 2419 | 2742
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.055 | 714 | 1554 | 2209 | 2493
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.06 | 670 | 1446 | 2032 | 2285
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.065 | 631 | 1352 | 1882 | 2110
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00291 | 0.00242 | 0.00495 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00458 | 0.00458 | 0.00242 | 0.00242 | 0.00242 | 0.60385 | 7.4278 | 258.366 | 0.07 | 596 | 1270 | 1753 | 1959
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.03 | 890 | 1416 | 2796 | 3960
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.035 | 821 | 1324 | 2477 | 3409
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.04 | 760 | 1241 | 2228 | 2995
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.045 | 705 | 1166 | 2028 | 2672
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.05 | 657 | 1097 | 1860 | 2411
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.055 | 613 | 1034 | 1719 | 2198
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.06 | 574 | 977 | 1597 | 2019
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.065 | 539 | 925 | 1492 | 1867
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00287 | 0.00242 | 0.0049 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00452 | 0.00452 | 0.00242 | 0.00242 | 0.00242 | 0.60439 | 8.2134 | 258.366 | 0.07 | 507 | 876 | 1400 | 1737
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.03 | 889 | 1414 | 2781 | 3948
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.035 | 820 | 1322 | 2465 | 3400
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.04 | 759 | 1239 | 2218 | 2987
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.045 | 704 | 1164 | 2019 | 2666
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.05 | 655 | 1095 | 1853 | 2406
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.055 | 612 | 1033 | 1713 | 2194
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.06 | 573 | 975 | 1592 | 2015
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.065 | 538 | 923 | 1487 | 1863
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00285 | 0.00242 | 0.00484 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00447 | 0.00447 | 0.00242 | 0.00242 | 0.00242 | 0.60521 | 8.219 | 258.366 | 0.07 | 506 | 875 | 1395 | 1734
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.03 | 887 | 1412 | 2767 | 3936
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.035 | 818 | 1320 | 2453 | 3391
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.04 | 757 | 1237 | 2209 | 2980
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.045 | 703 | 1162 | 2011 | 2659
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.05 | 654 | 1093 | 1846 | 2401
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.055 | 611 | 1031 | 1707 | 2189
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.06 | 572 | 974 | 1586 | 2011
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.065 | 537 | 921 | 1482 | 1860
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00282 | 0.00242 | 0.00479 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00443 | 0.00443 | 0.00242 | 0.00242 | 0.00242 | 0.60617 | 8.2255 | 258.366 | 0.07 | 505 | 873 | 1391 | 1731
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.03 | 887 | 1412 | 2767 | 3936
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.035 | 818 | 1320 | 2453 | 3391
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.04 | 757 | 1237 | 2209 | 2980
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.045 | 703 | 1162 | 2011 | 2659
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.05 | 654 | 1093 | 1846 | 2401
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.055 | 611 | 1031 | 1707 | 2189
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.06 | 572 | 974 | 1586 | 2011
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.065 | 537 | 921 | 1482 | 1860
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00279 | 0.00242 | 0.00474 | 0.00242 | 0.00242 | 0.00242 | 0.00242 | 0.00438 | 0.00438 | 0.00242 | 0.00242 | 0.00242 | 0.60701 | 8.2312 | 258.366 | 0.07 | 505 | 873 | 1391 | 1731
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.03 | 883 | 1520 | 3045 | 4032
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.035 | 816 | 1408 | 2668 | 3456
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.04 | 757 | 1311 | 2378 | 3024
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.045 | 704 | 1226 | 2148 | 2688
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.05 | 656 | 1149 | 1959 | 2419
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.055 | 614 | 1081 | 1801 | 2199
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.06 | 575 | 1018 | 1666 | 2016
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.065 | 541 | 962 | 1551 | 1861
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00267 | 0.00241 | 0.00452 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.0042 | 0.0042 | 0.00241 | 0.00241 | 0.00241 | 0.61071 | 7.9202 | 272.816 | 0.07 | 510 | 912 | 1450 | 1728
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.03 | 775 | 1239 | 1895 | 3133
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.035 | 712 | 1155 | 1736 | 2739
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.04 | 656 | 1079 | 1603 | 2438
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.045 | 607 | 1011 | 1488 | 2199
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.05 | 564 | 948 | 1389 | 2003
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.055 | 525 | 892 | 1301 | 1839
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.06 | 491 | 840 | 1223 | 1701
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.065 | 460 | 794 | 1153 | 1582
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00264 | 0.00241 | 0.00448 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00415 | 0.00415 | 0.00241 | 0.00241 | 0.00241 | 0.61189 | 8.7623 | 272.816 | 0.07 | 432 | 751 | 1090 | 1478
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.03 | 774 | 1238 | 1881 | 3121
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.035 | 711 | 1153 | 1724 | 2731
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.04 | 655 | 1078 | 1593 | 2431
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.045 | 606 | 1009 | 1481 | 2193
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.05 | 563 | 947 | 1382 | 1998
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.055 | 524 | 890 | 1295 | 1835
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.06 | 490 | 839 | 1217 | 1697
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.065 | 459 | 792 | 1148 | 1579
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00261 | 0.00241 | 0.00443 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00411 | 0.00411 | 0.00241 | 0.00241 | 0.00241 | 0.61347 | 8.7737 | 272.816 | 0.07 | 431 | 750 | 1086 | 1475
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.03 | 771 | 1234 | 1853 | 3099
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.035 | 708 | 1150 | 1702 | 2713
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.04 | 653 | 1074 | 1575 | 2416
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.045 | 604 | 1006 | 1465 | 2180
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.05 | 561 | 944 | 1368 | 1988
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.055 | 522 | 887 | 1283 | 1826
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.06 | 488 | 836 | 1207 | 1690
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.065 | 457 | 789 | 1139 | 1572
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00259 | 0.00241 | 0.00439 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00406 | 0.00406 | 0.00241 | 0.00241 | 0.00241 | 0.61529 | 8.7867 | 272.816 | 0.07 | 430 | 747 | 1077 | 1469
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.03 | 770 | 1232 | 1840 | 3088
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.035 | 707 | 1148 | 1691 | 2704
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.04 | 652 | 1073 | 1566 | 2409
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.045 | 603 | 1004 | 1457 | 2174
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.05 | 560 | 942 | 1362 | 1982
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.055 | 521 | 886 | 1277 | 1822
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.06 | 487 | 835 | 1202 | 1686
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.065 | 456 | 788 | 1134 | 1569
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00256 | 0.00241 | 0.00434 | 0.00241 | 0.00241 | 0.00241 | 0.00241 | 0.00402 | 0.00402 | 0.00241 | 0.00241 | 0.00241 | 0.61729 | 8.8009 | 272.816 | 0.07 | 429 | 746 | 1073 | 1466

## 50%_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.03 | 2980 | 10820 | 11247 | 11691
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.035 | 2853 | 9275 | 9641 | 10021
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.04 | 2734 | 8115 | 8436 | 8768
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.045 | 2621 | 7214 | 7498 | 7794
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.05 | 2515 | 6492 | 6748 | 7015
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.055 | 2415 | 5902 | 6135 | 6377
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.06 | 2321 | 5410 | 5624 | 5846
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.065 | 2232 | 4994 | 5191 | 5396
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00609 | 0.00504 | 0.01047 | 0.00404 | 0.00302 | 0.00337 | 0.00407 | 0.00967 | 0.00967 | 0.00302 | 0.00313 | 0.00313 | 0.33634 | 3.8736 | 186.116 | 0.07 | 2149 | 4637 | 4820 | 5010
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.03 | 2621 | 9707 | 10139 | 10591
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.035 | 2497 | 8320 | 8691 | 9078
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.04 | 2381 | 7280 | 7605 | 7943
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.045 | 2273 | 6471 | 6760 | 7061
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.05 | 2172 | 5824 | 6084 | 6355
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.055 | 2078 | 5295 | 5531 | 5777
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.06 | 1989 | 4853 | 5070 | 5296
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.065 | 1906 | 4480 | 4680 | 4888
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00603 | 0.00499 | 0.01035 | 0.00399 | 0.00302 | 0.00335 | 0.00402 | 0.00957 | 0.00957 | 0.00302 | 0.0031 | 0.0031 | 0.34895 | 4.3609 | 186.116 | 0.07 | 1828 | 4160 | 4345 | 4539
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.03 | 2563 | 9522 | 9955 | 10408
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.035 | 2439 | 8162 | 8533 | 8921
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.04 | 2325 | 7142 | 7466 | 7806
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.045 | 2218 | 6348 | 6637 | 6939
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.05 | 2117 | 5713 | 5973 | 6245
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.055 | 2024 | 5194 | 5430 | 5677
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.06 | 1936 | 4761 | 4978 | 5204
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.065 | 1854 | 4395 | 4595 | 4804
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00597 | 0.00494 | 0.01025 | 0.00395 | 0.00302 | 0.00332 | 0.00398 | 0.00946 | 0.00946 | 0.00302 | 0.00308 | 0.00308 | 0.36308 | 4.4483 | 186.116 | 0.07 | 1777 | 4081 | 4267 | 4461
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.03 | 2501 | 9323 | 9757 | 10211
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.035 | 2378 | 7991 | 8363 | 8753
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.04 | 2264 | 6992 | 7318 | 7658
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.045 | 2158 | 6215 | 6505 | 6808
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.05 | 2059 | 5594 | 5854 | 6127
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.055 | 1966 | 5085 | 5322 | 5570
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.06 | 1880 | 4662 | 4879 | 5106
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.065 | 1799 | 4303 | 4503 | 4713
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00591 | 0.00489 | 0.01013 | 0.0039 | 0.00302 | 0.00327 | 0.00393 | 0.00936 | 0.00936 | 0.00302 | 0.00303 | 0.00303 | 0.38001 | 4.5508 | 186.116 | 0.07 | 1723 | 3996 | 4182 | 4376
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.03 | 2424 | 9074 | 9509 | 9964
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.035 | 2302 | 7778 | 8150 | 8541
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.04 | 2189 | 6805 | 7132 | 7473
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.045 | 2084 | 6049 | 6339 | 6643
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.05 | 1987 | 5444 | 5705 | 5979
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.055 | 1895 | 4949 | 5187 | 5435
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.06 | 1810 | 4537 | 4754 | 4982
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.065 | 1731 | 4188 | 4389 | 4599
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00583 | 0.00483 | 0.01002 | 0.00385 | 0.00302 | 0.00324 | 0.00388 | 0.00925 | 0.00925 | 0.00302 | 0.00302 | 0.00302 | 0.40267 | 4.6845 | 186.116 | 0.07 | 1656 | 3889 | 4075 | 4270
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.03 | 1962 | 7464 | 7869 | 8295
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.035 | 1854 | 6398 | 6744 | 7110
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.04 | 1754 | 5598 | 5901 | 6221
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.045 | 1661 | 4976 | 5246 | 5530
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.05 | 1576 | 4478 | 4721 | 4977
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.055 | 1497 | 4071 | 4292 | 4525
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.06 | 1424 | 3732 | 3934 | 4148
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.065 | 1356 | 3445 | 3632 | 3829
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00532 | 0.00443 | 0.00912 | 0.00353 | 0.00299 | 0.00299 | 0.00356 | 0.00844 | 0.00844 | 0.00299 | 0.00299 | 0.00299 | 0.53025 | 5.2829 | 200.566 | 0.07 | 1293 | 3199 | 3372 | 3555
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.03 | 1742 | 6698 | 7102 | 7529
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.035 | 1637 | 5741 | 6087 | 6454
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.04 | 1542 | 5024 | 5326 | 5647
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.045 | 1454 | 4465 | 4734 | 5020
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.05 | 1373 | 4019 | 4261 | 4518
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.055 | 1300 | 3653 | 3874 | 4107
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.06 | 1232 | 3349 | 3551 | 3765
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.065 | 1169 | 3091 | 3278 | 3475
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00527 | 0.00438 | 0.00901 | 0.00349 | 0.00299 | 0.00299 | 0.00353 | 0.00836 | 0.00836 | 0.00299 | 0.00299 | 0.00299 | 0.53265 | 5.8522 | 200.566 | 0.07 | 1111 | 2871 | 3044 | 3227
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.03 | 1735 | 6673 | 7077 | 7505
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.035 | 1631 | 5720 | 6066 | 6432
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.04 | 1535 | 5005 | 5308 | 5628
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.045 | 1447 | 4449 | 4718 | 5003
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.05 | 1367 | 4004 | 4246 | 4503
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.055 | 1293 | 3640 | 3860 | 4093
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.06 | 1226 | 3337 | 3538 | 3752
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.065 | 1163 | 3080 | 3266 | 3464
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00521 | 0.00434 | 0.00893 | 0.00345 | 0.00299 | 0.00299 | 0.00348 | 0.00826 | 0.00826 | 0.00299 | 0.00299 | 0.00299 | 0.53554 | 5.868 | 200.566 | 0.07 | 1106 | 2860 | 3033 | 3216
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.03 | 1728 | 6649 | 7052 | 7480
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.035 | 1624 | 5699 | 6045 | 6411
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.04 | 1528 | 4986 | 5289 | 5610
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.045 | 1441 | 4432 | 4701 | 4987
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.05 | 1361 | 3989 | 4231 | 4488
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.055 | 1287 | 3626 | 3847 | 4080
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.06 | 1220 | 3324 | 3526 | 3740
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.065 | 1157 | 3069 | 3255 | 3452
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00514 | 0.00429 | 0.00884 | 0.00342 | 0.00299 | 0.00299 | 0.00345 | 0.00817 | 0.00817 | 0.00299 | 0.00299 | 0.00299 | 0.53873 | 5.8855 | 200.566 | 0.07 | 1100 | 2849 | 3022 | 3206
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.03 | 1721 | 6624 | 7027 | 7455
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.035 | 1617 | 5678 | 6023 | 6390
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.04 | 1522 | 4968 | 5271 | 5591
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.045 | 1434 | 4416 | 4685 | 4970
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.05 | 1354 | 3974 | 4216 | 4473
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.055 | 1281 | 3613 | 3833 | 4066
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.06 | 1214 | 3312 | 3514 | 3728
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.065 | 1152 | 3057 | 3243 | 3441
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0051 | 0.00423 | 0.00873 | 0.00337 | 0.00299 | 0.00299 | 0.00341 | 0.00809 | 0.00809 | 0.00299 | 0.00299 | 0.00299 | 0.54294 | 5.9085 | 200.566 | 0.07 | 1094 | 2839 | 3012 | 3195
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.03 | 1584 | 6101 | 6477 | 6876
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.035 | 1487 | 5230 | 5552 | 5894
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.04 | 1399 | 4576 | 4858 | 5157
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.045 | 1318 | 4068 | 4318 | 4584
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.05 | 1244 | 3661 | 3886 | 4126
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.055 | 1176 | 3328 | 3533 | 3751
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.06 | 1113 | 3051 | 3239 | 3438
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.065 | 1056 | 2816 | 2989 | 3174
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00471 | 0.00393 | 0.00807 | 0.00314 | 0.00297 | 0.00297 | 0.00317 | 0.00749 | 0.00749 | 0.00297 | 0.00297 | 0.00297 | 0.58398 | 5.9841 | 215.016 | 0.07 | 1003 | 2615 | 2776 | 2947
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.03 | 1381 | 4566 | 5735 | 6133
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.035 | 1289 | 3962 | 4916 | 5257
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.04 | 1206 | 3503 | 4302 | 4600
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.045 | 1130 | 3142 | 3824 | 4089
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.05 | 1061 | 2849 | 3441 | 3680
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.055 | 999 | 2607 | 3128 | 3345
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.06 | 942 | 2402 | 2868 | 3066
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.065 | 890 | 2228 | 2647 | 2831
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00466 | 0.00388 | 0.00798 | 0.00309 | 0.00297 | 0.00297 | 0.00312 | 0.00741 | 0.00741 | 0.00297 | 0.00297 | 0.00297 | 0.5989 | 6.698 | 215.016 | 0.07 | 843 | 2077 | 2458 | 2628
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00462 | 0.00384 | 0.00791 | 0.00306 | 0.00297 | 0.00297 | 0.00309 | 0.00732 | 0.00732 | 0.00297 | 0.00297 | 0.00297 | 0.61794 | 6.8036 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00458 | 0.0038 | 0.00782 | 0.00303 | 0.00297 | 0.00297 | 0.00306 | 0.00725 | 0.00725 | 0.00297 | 0.00297 | 0.00297 | 0.61766 | 6.8021 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.03 | 1357 | 4350 | 5642 | 6039
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.035 | 1265 | 3784 | 4836 | 5176
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.04 | 1182 | 3353 | 4232 | 4529
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.045 | 1107 | 3012 | 3761 | 4026
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.05 | 1039 | 2735 | 3385 | 3623
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.055 | 978 | 2506 | 3077 | 3294
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.06 | 922 | 2311 | 2821 | 3020
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.065 | 870 | 2146 | 2604 | 2787
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00451 | 0.00377 | 0.00774 | 0.003 | 0.00297 | 0.00297 | 0.00303 | 0.00717 | 0.00717 | 0.00297 | 0.00297 | 0.00297 | 0.6173 | 6.8001 | 215.016 | 0.07 | 824 | 2001 | 2418 | 2588
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.03 | 1318 | 4480 | 5462 | 5835
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.035 | 1231 | 3879 | 4682 | 5002
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.04 | 1152 | 3424 | 4097 | 4376
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.045 | 1081 | 3066 | 3642 | 3890
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.05 | 1016 | 2776 | 3277 | 3501
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.055 | 957 | 2537 | 2980 | 3183
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.06 | 903 | 2336 | 2731 | 2918
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.065 | 853 | 2164 | 2521 | 2693
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00423 | 0.00353 | 0.00723 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00669 | 0.00669 | 0.00294 | 0.00294 | 0.00294 | 0.61689 | 6.6028 | 229.466 | 0.07 | 808 | 2017 | 2341 | 2501
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00418 | 0.00348 | 0.00715 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00661 | 0.00661 | 0.00294 | 0.00294 | 0.00294 | 0.61673 | 7.2968 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00414 | 0.00345 | 0.00708 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00656 | 0.00656 | 0.00294 | 0.00294 | 0.00294 | 0.61664 | 7.2963 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0041 | 0.00341 | 0.00699 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00648 | 0.00648 | 0.00294 | 0.00294 | 0.00294 | 0.61649 | 7.2954 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.03 | 1164 | 3063 | 4629 | 5246
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.035 | 1081 | 2709 | 3990 | 4497
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.04 | 1007 | 2435 | 3508 | 3935
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.045 | 940 | 2212 | 3131 | 3497
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.05 | 879 | 2029 | 2828 | 3148
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.055 | 825 | 1873 | 2579 | 2862
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.06 | 776 | 1739 | 2370 | 2623
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.065 | 731 | 1623 | 2192 | 2421
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00407 | 0.00337 | 0.00692 | 0.00294 | 0.00294 | 0.00294 | 0.00294 | 0.00641 | 0.00641 | 0.00294 | 0.00294 | 0.00294 | 0.61671 | 7.2967 | 229.466 | 0.07 | 690 | 1522 | 2040 | 2248
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.03 | 1142 | 3339 | 4722 | 5117
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.035 | 1062 | 2927 | 4053 | 4386
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.04 | 991 | 2610 | 3549 | 3838
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.045 | 927 | 2357 | 3157 | 3411
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.05 | 868 | 2150 | 2843 | 3070
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.055 | 816 | 1976 | 2586 | 2791
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.06 | 768 | 1829 | 2372 | 2558
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.065 | 724 | 1702 | 2190 | 2362
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00383 | 0.00318 | 0.00652 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00605 | 0.00605 | 0.00292 | 0.00292 | 0.00292 | 0.61706 | 7.0562 | 243.916 | 0.07 | 685 | 1592 | 2034 | 2193
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0038 | 0.00315 | 0.00645 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00597 | 0.00597 | 0.00292 | 0.00292 | 0.00292 | 0.61738 | 7.801 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00312 | 0.00639 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00591 | 0.00591 | 0.00292 | 0.00292 | 0.00292 | 0.61755 | 7.802 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.03 | 1007 | 1928 | 3589 | 4588
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.035 | 932 | 1764 | 3134 | 3933
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.04 | 865 | 1626 | 2785 | 3441
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.045 | 805 | 1508 | 2508 | 3059
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.05 | 751 | 1406 | 2282 | 2753
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.055 | 703 | 1316 | 2094 | 2503
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.06 | 659 | 1235 | 1935 | 2294
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.065 | 620 | 1164 | 1798 | 2118
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0037 | 0.00308 | 0.00632 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00585 | 0.00585 | 0.00292 | 0.00292 | 0.00292 | 0.61764 | 7.8026 | 243.916 | 0.07 | 584 | 1099 | 1679 | 1966
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.03 | 1006 | 1909 | 3574 | 4582
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.035 | 930 | 1749 | 3121 | 3927
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.04 | 863 | 1613 | 2774 | 3436
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.045 | 803 | 1497 | 2499 | 3055
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.05 | 749 | 1396 | 2274 | 2749
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.055 | 701 | 1307 | 2087 | 2499
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.06 | 658 | 1227 | 1929 | 2291
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.065 | 618 | 1156 | 1793 | 2115
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00367 | 0.00304 | 0.00624 | 0.00292 | 0.00292 | 0.00292 | 0.00292 | 0.00579 | 0.00579 | 0.00292 | 0.00292 | 0.00292 | 0.61811 | 7.8055 | 243.916 | 0.07 | 583 | 1092 | 1675 | 1964
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.03 | 994 | 2306 | 3778 | 4504
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.035 | 922 | 2065 | 3274 | 3861
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.04 | 857 | 1874 | 2891 | 3378
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.045 | 799 | 1716 | 2591 | 3003
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.05 | 746 | 1583 | 2347 | 2702
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.055 | 699 | 1469 | 2146 | 2457
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.06 | 657 | 1371 | 1977 | 2252
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.065 | 618 | 1284 | 1832 | 2079
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00349 | 0.00291 | 0.00594 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00549 | 0.00549 | 0.00291 | 0.00291 | 0.00291 | 0.61996 | 7.5263 | 258.366 | 0.07 | 583 | 1207 | 1708 | 1930
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.03 | 875 | 1393 | 2637 | 3829
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.035 | 806 | 1302 | 2348 | 3306
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.04 | 746 | 1220 | 2121 | 2911
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.045 | 692 | 1145 | 1936 | 2602
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.05 | 644 | 1077 | 1781 | 2352
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.055 | 601 | 1015 | 1650 | 2147
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.06 | 562 | 958 | 1536 | 1974
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.065 | 528 | 906 | 1437 | 1828
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00345 | 0.00291 | 0.00588 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00543 | 0.00543 | 0.00291 | 0.00291 | 0.00291 | 0.62055 | 8.3225 | 258.366 | 0.07 | 497 | 859 | 1350 | 1702
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.03 | 874 | 1391 | 2622 | 3818
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.035 | 805 | 1300 | 2336 | 3296
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.04 | 744 | 1218 | 2111 | 2903
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.045 | 691 | 1143 | 1928 | 2595
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.05 | 643 | 1075 | 1774 | 2347
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.055 | 600 | 1013 | 1644 | 2142
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.06 | 561 | 956 | 1531 | 1970
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.065 | 527 | 905 | 1432 | 1824
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00342 | 0.00291 | 0.00581 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00537 | 0.00537 | 0.00291 | 0.00291 | 0.00291 | 0.62143 | 8.3284 | 258.366 | 0.07 | 496 | 857 | 1346 | 1699
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.03 | 872 | 1389 | 2608 | 3806
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.035 | 804 | 1298 | 2325 | 3287
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.04 | 743 | 1216 | 2102 | 2895
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.045 | 689 | 1141 | 1920 | 2589
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.05 | 641 | 1073 | 1767 | 2341
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.055 | 599 | 1011 | 1637 | 2138
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.06 | 560 | 955 | 1525 | 1966
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.065 | 526 | 903 | 1427 | 1820
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00339 | 0.00291 | 0.00575 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00531 | 0.00531 | 0.00291 | 0.00291 | 0.00291 | 0.62248 | 8.3354 | 258.366 | 0.07 | 495 | 855 | 1341 | 1695
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.03 | 872 | 1389 | 2608 | 3806
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.035 | 804 | 1298 | 2325 | 3287
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.04 | 743 | 1216 | 2102 | 2895
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.045 | 689 | 1141 | 1920 | 2589
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.05 | 641 | 1073 | 1767 | 2341
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.055 | 599 | 1011 | 1637 | 2138
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.06 | 560 | 955 | 1525 | 1966
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.065 | 526 | 903 | 1427 | 1820
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00335 | 0.00291 | 0.00568 | 0.00291 | 0.00291 | 0.00291 | 0.00291 | 0.00525 | 0.00525 | 0.00291 | 0.00291 | 0.00291 | 0.62338 | 8.3415 | 258.366 | 0.07 | 495 | 855 | 1341 | 1695
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.03 | 868 | 1377 | 2894 | 3952
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.035 | 801 | 1290 | 2546 | 3390
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.04 | 742 | 1210 | 2277 | 2968
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.045 | 690 | 1138 | 2061 | 2640
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.05 | 643 | 1072 | 1884 | 2377
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.055 | 601 | 1011 | 1735 | 2161
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.06 | 563 | 956 | 1608 | 1981
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.065 | 529 | 905 | 1499 | 1830
| 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00321 | 0.0029 | 0.00543 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00504 | 0.00504 | 0.0029 | 0.0029 | 0.0029 | 0.6274 | 8.0277 | 272.816 | 0.07 | 498 | 859 | 1403 | 1699
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.03 | 761 | 1219 | 1730 | 2998
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.035 | 699 | 1135 | 1602 | 2632
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.04 | 644 | 1060 | 1492 | 2351
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.045 | 595 | 992 | 1394 | 2126
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.05 | 552 | 930 | 1307 | 1941
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.055 | 514 | 874 | 1229 | 1786
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.06 | 480 | 823 | 1159 | 1655
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.065 | 450 | 777 | 1096 | 1542
| 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00316 | 0.0029 | 0.00537 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00498 | 0.00498 | 0.0029 | 0.0029 | 0.0029 | 0.62866 | 8.8816 | 272.816 | 0.07 | 422 | 735 | 1038 | 1442
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.03 | 760 | 1217 | 1717 | 2987
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.035 | 697 | 1133 | 1591 | 2624
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.04 | 643 | 1058 | 1483 | 2343
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.045 | 594 | 990 | 1386 | 2120
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.05 | 551 | 929 | 1301 | 1936
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.055 | 513 | 873 | 1223 | 1782
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.06 | 479 | 822 | 1154 | 1651
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.065 | 449 | 776 | 1091 | 1538
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00313 | 0.0029 | 0.00531 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00493 | 0.00493 | 0.0029 | 0.0029 | 0.0029 | 0.63036 | 8.8936 | 272.816 | 0.07 | 422 | 734 | 1034 | 1439
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.03 | 758 | 1214 | 1689 | 2964
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.035 | 695 | 1130 | 1569 | 2606
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.04 | 641 | 1055 | 1464 | 2329
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.045 | 592 | 987 | 1371 | 2108
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.05 | 549 | 926 | 1287 | 1926
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.055 | 511 | 870 | 1212 | 1773
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.06 | 478 | 819 | 1144 | 1644
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.065 | 447 | 773 | 1082 | 1532
| 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0031 | 0.0029 | 0.00527 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00487 | 0.00487 | 0.0029 | 0.0029 | 0.0029 | 0.63231 | 8.9073 | 272.816 | 0.07 | 420 | 731 | 1026 | 1433
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.03 | 756 | 1212 | 1676 | 2953
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.035 | 694 | 1129 | 1558 | 2597
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.04 | 639 | 1053 | 1455 | 2322
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.045 | 591 | 985 | 1363 | 2102
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.05 | 548 | 924 | 1280 | 1921
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.055 | 511 | 868 | 1206 | 1769
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.06 | 477 | 818 | 1138 | 1640
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.065 | 446 | 772 | 1077 | 1528
| 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00308 | 0.0029 | 0.00521 | 0.0029 | 0.0029 | 0.0029 | 0.0029 | 0.00483 | 0.00483 | 0.0029 | 0.0029 | 0.0029 | 0.63444 | 8.9223 | 272.816 | 0.07 | 419 | 730 | 1021 | 1430

## thickness_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.025 | 5362 | 20986 | 21550 | 22129
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.03 | 5197 | 17489 | 17958 | 18440
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.035 | 5039 | 14990 | 15393 | 15806
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.04 | 4887 | 13116 | 13469 | 13830
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.045 | 4742 | 11659 | 11972 | 12294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.05 | 4603 | 10493 | 10775 | 11064
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.055 | 4469 | 9539 | 9795 | 10058
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.06 | 4341 | 8744 | 8979 | 9220
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.065 | 4218 | 8072 | 8288 | 8511
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 150 | 0 | 80 | 11 | 0.00547 | 0.00453 | 0.00948 | 0.0036 | 0.00206 | 0.00302 | 0.00363 | 0.00876 | 0.00876 | 0.0024 | 0.0028 | 0.0028 | 0.1885 | 2.6529 | 157.216 | 0.07 | 4100 | 7495 | 7696 | 7903
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.025 | 5095 | 20052 | 20607 | 21178
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.03 | 4933 | 16710 | 17173 | 17648
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.035 | 4779 | 14323 | 14720 | 15127
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.04 | 4632 | 12533 | 12880 | 13236
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.045 | 4490 | 11140 | 11449 | 11765
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.05 | 4355 | 10026 | 10304 | 10589
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.055 | 4225 | 9115 | 9367 | 9626
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.06 | 4101 | 8355 | 8586 | 8824
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.065 | 3982 | 7712 | 7926 | 8145
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.25 | 150 | 0 | 80 | 11 | 0.00524 | 0.00434 | 0.00905 | 0.00344 | 0.00205 | 0.00289 | 0.00347 | 0.00837 | 0.00837 | 0.0023 | 0.00268 | 0.00268 | 0.18991 | 2.732 | 160.8285 | 0.07 | 3868 | 7162 | 7360 | 7563
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.025 | 4830 | 19125 | 19672 | 20235
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.03 | 4672 | 15937 | 16393 | 16862
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.035 | 4522 | 13661 | 14051 | 14453
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.04 | 4378 | 11953 | 12295 | 12647
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.045 | 4241 | 10625 | 10929 | 11241
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.05 | 4109 | 9562 | 9836 | 10117
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.055 | 3983 | 8693 | 8942 | 9198
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.06 | 3863 | 7969 | 8197 | 8431
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.065 | 3748 | 7356 | 7566 | 7783
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.5 | 150 | 0 | 80 | 11 | 0.00502 | 0.00415 | 0.00866 | 0.0033 | 0.00205 | 0.00277 | 0.00333 | 0.008 | 0.008 | 0.00221 | 0.00257 | 0.00257 | 0.19224 | 2.8185 | 164.441 | 0.07 | 3638 | 6830 | 7026 | 7227
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.025 | 4582 | 18248 | 18786 | 19341
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.03 | 4428 | 15206 | 15655 | 16118
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.035 | 4281 | 13034 | 13419 | 13815
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.04 | 4141 | 11405 | 11741 | 12088
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.045 | 4008 | 10138 | 10437 | 10745
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.05 | 3880 | 9124 | 9393 | 9671
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.055 | 3758 | 8294 | 8539 | 8791
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.06 | 3642 | 7603 | 7828 | 8059
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.065 | 3530 | 7018 | 7226 | 7439
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10.75 | 150 | 0 | 80 | 11 | 0.00481 | 0.00398 | 0.0083 | 0.00317 | 0.00204 | 0.00266 | 0.0032 | 0.00767 | 0.00767 | 0.00212 | 0.00247 | 0.00247 | 0.19583 | 2.915 | 168.0535 | 0.07 | 3424 | 6517 | 6709 | 6908
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.025 | 4312 | 17299 | 17831 | 18379
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.03 | 4162 | 14416 | 14859 | 15316
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.035 | 4019 | 12356 | 12736 | 13128
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.04 | 3883 | 10812 | 11144 | 11487
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.045 | 3753 | 9610 | 9906 | 10211
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.05 | 3630 | 8649 | 8915 | 9190
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.055 | 3512 | 7863 | 8105 | 8354
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.06 | 3399 | 7208 | 7430 | 7658
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.065 | 3292 | 6653 | 6858 | 7069
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11 | 150 | 0 | 80 | 11 | 0.00462 | 0.00383 | 0.00796 | 0.00304 | 0.00203 | 0.00255 | 0.00308 | 0.00736 | 0.00736 | 0.00204 | 0.00237 | 0.00237 | 0.20141 | 3.0276 | 171.666 | 0.07 | 3189 | 6178 | 6368 | 6564
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.025 | 4028 | 16293 | 16819 | 17363
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.03 | 3882 | 13577 | 14016 | 14469
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.035 | 3742 | 11638 | 12014 | 12402
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.04 | 3610 | 10183 | 10512 | 10852
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.045 | 3484 | 9052 | 9344 | 9646
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.05 | 3365 | 8146 | 8410 | 8681
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.055 | 3251 | 7406 | 7645 | 7892
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.06 | 3142 | 6789 | 7008 | 7234
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.065 | 3039 | 6266 | 6469 | 6678
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.25 | 150 | 0 | 80 | 11 | 0.00445 | 0.00368 | 0.00765 | 0.00293 | 0.00202 | 0.00246 | 0.00296 | 0.00707 | 0.00707 | 0.00202 | 0.00228 | 0.00228 | 0.21155 | 3.176 | 175.2785 | 0.07 | 2941 | 5819 | 6007 | 6201
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.025 | 3737 | 15254 | 15776 | 16315
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.03 | 3594 | 12712 | 13146 | 13596
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.035 | 3459 | 10896 | 11268 | 11653
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.04 | 3331 | 9534 | 9860 | 10197
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.045 | 3209 | 8475 | 8764 | 9064
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.05 | 3094 | 7627 | 7888 | 8157
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.055 | 2984 | 6934 | 7171 | 7416
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.06 | 2880 | 6356 | 6573 | 6798
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.065 | 2781 | 5867 | 6068 | 6275
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.5 | 150 | 0 | 80 | 11 | 0.00428 | 0.00354 | 0.00736 | 0.00282 | 0.00202 | 0.00237 | 0.00285 | 0.00681 | 0.00681 | 0.00202 | 0.0022 | 0.0022 | 0.22604 | 3.3586 | 178.891 | 0.07 | 2687 | 5448 | 5634 | 5827
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.025 | 3419 | 14104 | 14621 | 15157
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.03 | 3280 | 11753 | 12184 | 12631
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.035 | 3148 | 10074 | 10443 | 10826
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.04 | 3025 | 8815 | 9138 | 9473
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.045 | 2907 | 7835 | 8123 | 8420
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.05 | 2797 | 7052 | 7310 | 7578
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.055 | 2692 | 6411 | 6646 | 6889
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.06 | 2593 | 5877 | 6092 | 6315
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.065 | 2499 | 5425 | 5623 | 5830
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 11.75 | 150 | 0 | 80 | 11 | 0.00412 | 0.00341 | 0.00708 | 0.00272 | 0.00201 | 0.00228 | 0.00275 | 0.00655 | 0.00655 | 0.00201 | 0.00212 | 0.00212 | 0.24781 | 3.5957 | 182.5035 | 0.07 | 2410 | 5037 | 5222 | 5413
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.025 | 3074 | 12837 | 13350 | 13884
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.03 | 2939 | 10698 | 11125 | 11570
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.035 | 2813 | 9169 | 9536 | 9917
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.04 | 2694 | 8023 | 8344 | 8677
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.045 | 2582 | 7132 | 7417 | 7713
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.05 | 2476 | 6419 | 6675 | 6942
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.055 | 2377 | 5835 | 6068 | 6311
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.06 | 2284 | 5349 | 5563 | 5785
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.065 | 2195 | 4937 | 5135 | 5340
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.07 | 2112 | 4585 | 4768 | 4959
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.025 | 2675 | 11330 | 11839 | 12372
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.03 | 2545 | 9441 | 9866 | 10310
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.035 | 2424 | 8093 | 8457 | 8837
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.04 | 2311 | 7081 | 7400 | 7732
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.045 | 2206 | 6294 | 6577 | 6873
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.05 | 2107 | 5665 | 5920 | 6186
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.055 | 2015 | 5150 | 5381 | 5624
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.06 | 1928 | 4721 | 4933 | 5155
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.065 | 1847 | 4358 | 4554 | 4758
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.25 | 150 | 0 | 80 | 11 | 0.00384 | 0.00318 | 0.00659 | 0.00254 | 0.00201 | 0.00213 | 0.00256 | 0.00609 | 0.00609 | 0.00201 | 0.00201 | 0.00201 | 0.3405 | 4.4005 | 189.7285 | 0.07 | 1771 | 4046 | 4228 | 4418
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.025 | 2145 | 9241 | 9745 | 10276
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.03 | 2023 | 7701 | 8121 | 8563
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.035 | 1911 | 6601 | 6961 | 7340
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.04 | 1807 | 5775 | 6090 | 6423
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.045 | 1712 | 5134 | 5414 | 5709
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.05 | 1623 | 4620 | 4872 | 5138
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.055 | 1541 | 4200 | 4429 | 4671
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.06 | 1466 | 3850 | 4060 | 4282
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.065 | 1396 | 3554 | 3748 | 3952
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.5 | 150 | 0 | 80 | 11 | 0.00371 | 0.00308 | 0.00636 | 0.00245 | 0.002 | 0.00206 | 0.00248 | 0.00588 | 0.00588 | 0.002 | 0.002 | 0.002 | 0.47513 | 5.3079 | 193.341 | 0.07 | 1331 | 3300 | 3480 | 3670
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.025 | 2046 | 8826 | 9320 | 9842
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.03 | 1927 | 7355 | 7767 | 8202
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.035 | 1817 | 6304 | 6657 | 7030
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.04 | 1717 | 5516 | 5825 | 6151
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.045 | 1624 | 4903 | 5178 | 5468
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.05 | 1539 | 4413 | 4660 | 4921
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.055 | 1460 | 4012 | 4236 | 4474
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.06 | 1387 | 3677 | 3883 | 4101
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.065 | 1319 | 3394 | 3585 | 3785
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12.75 | 150 | 0 | 80 | 11 | 0.00358 | 0.00298 | 0.00615 | 0.00238 | 0.00199 | 0.00199 | 0.0024 | 0.00569 | 0.00569 | 0.00199 | 0.00199 | 0.00199 | 0.48101 | 5.4509 | 196.9535 | 0.07 | 1257 | 3152 | 3329 | 3515
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.025 | 1950 | 8423 | 8908 | 9421
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.03 | 1833 | 7019 | 7423 | 7851
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.035 | 1727 | 6016 | 6363 | 6729
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.04 | 1629 | 5264 | 5568 | 5888
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.045 | 1540 | 4679 | 4949 | 5234
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.05 | 1457 | 4212 | 4454 | 4711
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.055 | 1381 | 3829 | 4049 | 4282
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.06 | 1311 | 3510 | 3712 | 3926
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.065 | 1246 | 3240 | 3426 | 3624
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.07 | 1186 | 3008 | 3181 | 3365
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.025 | 1856 | 8029 | 8505 | 9010
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.03 | 1743 | 6691 | 7088 | 7508
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.035 | 1639 | 5735 | 6075 | 6435
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.04 | 1545 | 5018 | 5316 | 5631
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.045 | 1458 | 4461 | 4725 | 5005
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.05 | 1378 | 4015 | 4253 | 4505
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.055 | 1305 | 3650 | 3866 | 4095
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.06 | 1237 | 3346 | 3544 | 3754
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.065 | 1175 | 3088 | 3271 | 3465
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.25 | 150 | 0 | 80 | 11 | 0.00337 | 0.0028 | 0.00576 | 0.00223 | 0.00199 | 0.00199 | 0.00225 | 0.00534 | 0.00534 | 0.00199 | 0.00199 | 0.00199 | 0.49625 | 5.7607 | 204.1785 | 0.07 | 1117 | 2868 | 3038 | 3218
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.025 | 1755 | 7603 | 8070 | 8566
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.03 | 1645 | 6336 | 6725 | 7138
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.035 | 1545 | 5431 | 5764 | 6118
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.04 | 1453 | 4752 | 5044 | 5353
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.045 | 1369 | 4224 | 4483 | 4759
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.05 | 1293 | 3802 | 4035 | 4283
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.055 | 1222 | 3456 | 3668 | 3893
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.06 | 1157 | 3168 | 3363 | 3569
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.065 | 1098 | 2924 | 3104 | 3294
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.5 | 150 | 0 | 80 | 11 | 0.00327 | 0.00272 | 0.00559 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00518 | 0.00518 | 0.00198 | 0.00198 | 0.00198 | 0.51029 | 5.9553 | 207.791 | 0.07 | 1043 | 2715 | 2882 | 3059
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.025 | 1644 | 6813 | 7585 | 8072
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.03 | 1537 | 5698 | 6321 | 6727
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.035 | 1440 | 4900 | 5418 | 5766
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.04 | 1352 | 4300 | 4741 | 5045
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.045 | 1271 | 3831 | 4214 | 4485
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.05 | 1198 | 3454 | 3793 | 4036
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.055 | 1131 | 3145 | 3448 | 3669
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.06 | 1069 | 2888 | 3161 | 3363
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.065 | 1013 | 2668 | 2917 | 3105
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13.75 | 150 | 0 | 80 | 11 | 0.00317 | 0.00264 | 0.00543 | 0.0021 | 0.00198 | 0.00198 | 0.00212 | 0.00503 | 0.00503 | 0.00198 | 0.00198 | 0.00198 | 0.53529 | 6.2159 | 211.4035 | 0.07 | 961 | 2481 | 2709 | 2883
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.025 | 1504 | 5616 | 6974 | 7451
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.03 | 1402 | 4739 | 5812 | 6209
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.035 | 1309 | 4105 | 4981 | 5322
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.045 | 1149 | 3246 | 3874 | 4140
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.05 | 1080 | 2940 | 3487 | 3726
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.055 | 1017 | 2688 | 3170 | 3387
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.06 | 959 | 2475 | 2906 | 3105
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.065 | 907 | 2294 | 2682 | 2866
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.07 | 859 | 2137 | 2491 | 2661
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.025 | 1449 | 5204 | 6725 | 7194
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.03 | 1349 | 4406 | 5604 | 5995
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.035 | 1258 | 3827 | 4803 | 5138
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.04 | 1176 | 3387 | 4203 | 4496
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.045 | 1102 | 3039 | 3736 | 3996
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.05 | 1035 | 2757 | 3362 | 3597
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.055 | 974 | 2524 | 3057 | 3270
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.06 | 918 | 2327 | 2802 | 2997
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.065 | 868 | 2158 | 2586 | 2767
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.25 | 150 | 0 | 80 | 11 | 0.00299 | 0.00249 | 0.00512 | 0.00198 | 0.00197 | 0.00197 | 0.00201 | 0.00474 | 0.00474 | 0.00197 | 0.00197 | 0.00197 | 0.58427 | 6.7373 | 218.6285 | 0.07 | 821 | 2013 | 2402 | 2569
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.025 | 1397 | 4804 | 6487 | 6948
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.03 | 1299 | 4083 | 5406 | 5790
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.035 | 1210 | 3558 | 4634 | 4963
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.04 | 1131 | 3156 | 4055 | 4342
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.045 | 1058 | 2839 | 3604 | 3860
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.05 | 993 | 2580 | 3244 | 3474
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.055 | 934 | 2365 | 2949 | 3158
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.06 | 880 | 2184 | 2703 | 2895
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.065 | 831 | 2028 | 2495 | 2672
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.5 | 150 | 0 | 80 | 11 | 0.00292 | 0.00242 | 0.00498 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00461 | 0.00461 | 0.00197 | 0.00197 | 0.00197 | 0.58406 | 6.8577 | 222.241 | 0.07 | 786 | 1893 | 2317 | 2481
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.025 | 1346 | 4417 | 6258 | 6710
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.03 | 1250 | 3770 | 5215 | 5592
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.035 | 1164 | 3296 | 4470 | 4793
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.04 | 1086 | 2933 | 3911 | 4194
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.045 | 1016 | 2644 | 3477 | 3728
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.05 | 953 | 2408 | 3129 | 3355
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.055 | 896 | 2211 | 2845 | 3050
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.06 | 843 | 2044 | 2607 | 2796
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.065 | 796 | 1901 | 2407 | 2581
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14.75 | 150 | 0 | 80 | 11 | 0.00284 | 0.00236 | 0.00484 | 0.00197 | 0.00197 | 0.00197 | 0.00197 | 0.00448 | 0.00448 | 0.00197 | 0.00197 | 0.00197 | 0.58383 | 6.978 | 225.8535 | 0.07 | 753 | 1776 | 2235 | 2397
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.025 | 1299 | 4043 | 5932 | 6486
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.03 | 1205 | 3468 | 4954 | 5405
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.035 | 1121 | 3043 | 4254 | 4633
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.045 | 977 | 2456 | 3318 | 3604
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.05 | 915 | 2242 | 2989 | 3243
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.055 | 860 | 2063 | 2720 | 2948
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.06 | 809 | 1910 | 2495 | 2703
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.065 | 763 | 1778 | 2305 | 2495
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.07 | 721 | 1663 | 2142 | 2317
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.025 | 1253 | 3680 | 5595 | 6272
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.03 | 1162 | 3174 | 4685 | 5227
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.035 | 1080 | 2800 | 4032 | 4480
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.04 | 1006 | 2508 | 3540 | 3920
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.045 | 940 | 2274 | 3156 | 3485
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.05 | 880 | 2081 | 2848 | 3136
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.055 | 826 | 1919 | 2595 | 2851
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.06 | 776 | 1779 | 2383 | 2614
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.065 | 732 | 1660 | 2203 | 2412
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.25 | 150 | 0 | 80 | 11 | 0.00269 | 0.00224 | 0.00459 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00425 | 0.00425 | 0.00196 | 0.00196 | 0.00196 | 0.58381 | 7.2211 | 233.0785 | 0.07 | 691 | 1554 | 2049 | 2240
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.025 | 1210 | 3330 | 5269 | 6068
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.03 | 1121 | 2891 | 4424 | 5057
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.035 | 1041 | 2563 | 3817 | 4334
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.04 | 969 | 2306 | 3359 | 3792
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.045 | 904 | 2098 | 2999 | 3371
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.05 | 846 | 1925 | 2711 | 3034
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.055 | 793 | 1779 | 2473 | 2758
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.06 | 746 | 1653 | 2273 | 2528
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.065 | 703 | 1544 | 2104 | 2334
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.5 | 150 | 0 | 80 | 11 | 0.00262 | 0.00218 | 0.00448 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00415 | 0.00415 | 0.00196 | 0.00196 | 0.00196 | 0.58394 | 7.3435 | 236.691 | 0.07 | 663 | 1448 | 1958 | 2167
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.025 | 1168 | 2964 | 4932 | 5863
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.03 | 1080 | 2596 | 4156 | 4886
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.035 | 1002 | 2317 | 3597 | 4188
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.04 | 932 | 2096 | 3172 | 3665
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.045 | 869 | 1915 | 2839 | 3257
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.05 | 812 | 1764 | 2570 | 2932
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.055 | 761 | 1634 | 2348 | 2665
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.06 | 715 | 1522 | 2161 | 2443
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.065 | 673 | 1425 | 2002 | 2255
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15.75 | 150 | 0 | 80 | 11 | 0.00256 | 0.00213 | 0.00436 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00404 | 0.00404 | 0.00195 | 0.00195 | 0.00195 | 0.58423 | 7.467 | 240.3035 | 0.07 | 635 | 1339 | 1865 | 2094
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.025 | 1129 | 2634 | 4625 | 5676
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.03 | 1043 | 2328 | 3911 | 4730
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.035 | 966 | 2094 | 3395 | 4054
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.045 | 837 | 1749 | 2692 | 3153
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.05 | 782 | 1617 | 2441 | 2838
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.055 | 732 | 1503 | 2234 | 2580
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.06 | 687 | 1404 | 2059 | 2365
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.065 | 647 | 1316 | 1909 | 2183
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.07 | 610 | 1239 | 1780 | 2027
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.025 | 1090 | 2290 | 4307 | 5489
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.03 | 1006 | 2051 | 3658 | 4574
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.035 | 931 | 1862 | 3186 | 3921
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.04 | 864 | 1708 | 2825 | 3431
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.045 | 805 | 1577 | 2540 | 3049
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.05 | 751 | 1465 | 2308 | 2745
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.055 | 703 | 1367 | 2116 | 2495
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.06 | 660 | 1281 | 1953 | 2287
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.065 | 621 | 1205 | 1814 | 2111
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.25 | 150 | 0 | 80 | 11 | 0.00244 | 0.00203 | 0.00415 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00385 | 0.00385 | 0.00195 | 0.00195 | 0.00195 | 0.58508 | 7.7159 | 247.5285 | 0.07 | 585 | 1136 | 1693 | 1960
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.025 | 1054 | 1979 | 4019 | 5317
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.03 | 972 | 1799 | 3427 | 4431
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.035 | 899 | 1652 | 2995 | 3798
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.04 | 834 | 1528 | 2664 | 3323
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.045 | 776 | 1420 | 2401 | 2954
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.05 | 724 | 1326 | 2187 | 2659
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.055 | 677 | 1244 | 2008 | 2417
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.06 | 635 | 1169 | 1856 | 2216
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.065 | 597 | 1102 | 1726 | 2045
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.5 | 150 | 0 | 80 | 11 | 0.00239 | 0.00198 | 0.00406 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00375 | 0.00375 | 0.00195 | 0.00195 | 0.00195 | 0.58573 | 7.842 | 251.141 | 0.07 | 563 | 1041 | 1613 | 1899
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.025 | 1018 | 1654 | 3717 | 5144
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.03 | 938 | 1536 | 3187 | 4286
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.035 | 867 | 1433 | 2797 | 3674
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.04 | 803 | 1340 | 2497 | 3215
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.045 | 747 | 1257 | 2257 | 2858
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.05 | 696 | 1182 | 2061 | 2572
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.055 | 651 | 1115 | 1896 | 2338
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.06 | 610 | 1052 | 1756 | 2143
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.065 | 573 | 996 | 1635 | 1978
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16.75 | 150 | 0 | 80 | 11 | 0.00233 | 0.00194 | 0.00396 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00367 | 0.00367 | 0.00194 | 0.00194 | 0.00194 | 0.58658 | 7.9696 | 254.7535 | 0.07 | 540 | 944 | 1529 | 1837
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.025 | 984 | 1540 | 3425 | 4896
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.03 | 906 | 1439 | 2955 | 4090
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.035 | 836 | 1347 | 2606 | 3513
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.04 | 774 | 1263 | 2336 | 3079
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.045 | 719 | 1187 | 2119 | 2742
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.05 | 670 | 1118 | 1939 | 2471
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.055 | 626 | 1055 | 1788 | 2249
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.06 | 586 | 997 | 1659 | 2063
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.065 | 551 | 943 | 1547 | 1906
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.07 | 519 | 895 | 1450 | 1772
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.025 | 952 | 1492 | 3142 | 4630
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.03 | 875 | 1392 | 2729 | 3882
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.035 | 807 | 1302 | 2420 | 3345
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.04 | 747 | 1220 | 2178 | 2939
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.045 | 693 | 1146 | 1983 | 2622
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.05 | 645 | 1078 | 1821 | 2367
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.055 | 602 | 1017 | 1683 | 2158
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.06 | 564 | 960 | 1564 | 1983
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.065 | 530 | 909 | 1462 | 1835
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.25 | 150 | 0 | 80 | 11 | 0.00223 | 0.00194 | 0.00378 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.0035 | 0.0035 | 0.00194 | 0.00194 | 0.00194 | 0.58929 | 8.2324 | 261.9785 | 0.07 | 498 | 861 | 1371 | 1707
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.025 | 920 | 1443 | 2848 | 4357
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.03 | 845 | 1346 | 2495 | 3667
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.035 | 778 | 1257 | 2228 | 3171
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.04 | 719 | 1177 | 2016 | 2795
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.045 | 667 | 1105 | 1843 | 2500
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.05 | 621 | 1039 | 1698 | 2262
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.055 | 579 | 979 | 1575 | 2066
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.06 | 542 | 924 | 1468 | 1901
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.065 | 508 | 874 | 1374 | 1761
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.5 | 150 | 0 | 80 | 11 | 0.00218 | 0.00194 | 0.0037 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00343 | 0.00343 | 0.00194 | 0.00194 | 0.00194 | 0.59095 | 8.3664 | 265.591 | 0.07 | 478 | 828 | 1292 | 1640
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.025 | 890 | 1399 | 2580 | 4106
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.03 | 817 | 1303 | 2281 | 3471
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.035 | 752 | 1217 | 2052 | 3011
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.04 | 694 | 1138 | 1867 | 2662
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.045 | 643 | 1067 | 1715 | 2387
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.05 | 598 | 1003 | 1586 | 2164
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.055 | 558 | 944 | 1475 | 1980
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.06 | 522 | 891 | 1378 | 1825
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.065 | 489 | 842 | 1293 | 1692
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17.75 | 150 | 0 | 80 | 11 | 0.00214 | 0.00194 | 0.00362 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00336 | 0.00336 | 0.00194 | 0.00194 | 0.00194 | 0.59297 | 8.5032 | 269.2035 | 0.07 | 460 | 797 | 1217 | 1578
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.025 | 861 | 1354 | 2302 | 3847
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.03 | 789 | 1260 | 2059 | 3267
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.035 | 725 | 1176 | 1869 | 2846
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.04 | 669 | 1099 | 1713 | 2525
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.045 | 620 | 1030 | 1583 | 2271
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.05 | 576 | 967 | 1470 | 2064
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.055 | 537 | 910 | 1372 | 1892
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.06 | 502 | 858 | 1286 | 1747
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.065 | 470 | 811 | 1210 | 1623
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00209 | 0.00193 | 0.00354 | 0.00193 | 0.00193 | 0.00193 | 0.00193 | 0.00329 | 0.00329 | 0.00193 | 0.00193 | 0.00193 | 0.5953 | 8.6428 | 272.816 | 0.07 | 442 | 767 | 1141 | 1515

## drop_panel_study
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | hdrop | heff | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast | *Assumes drop panels are 1/6 length of span in each direction
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | in | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 15 | 12.99 | 150 | 0 | 80 | 11 | 0.00418 | 0.0021 | 0.0043 | 0.00275 | 0.00201 | 0.00231 | 0.00278 | 0.00398 | 0.00398 | 0.00201 | 0.00215 | 0.00215 | 0.20017 | 3.5847 | 200.4215 | 0.04 | 2772 | 8066 | 8360 | 8665
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 16 | 13.32 | 150 | 0 | 80 | 11 | 0.00424 | 0.00195 | 0.00377 | 0.0028 | 0.00201 | 0.00235 | 0.00283 | 0.00349 | 0.00349 | 0.00201 | 0.00218 | 0.00218 | 0.19368 | 3.6185 | 205.19 | 0.04 | 2673 | 7802 | 8090 | 8388
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 17 | 13.65 | 150 | 0 | 80 | 11 | 0.00431 | 0.00194 | 0.00335 | 0.00284 | 0.00201 | 0.00238 | 0.00287 | 0.00311 | 0.00311 | 0.00201 | 0.00221 | 0.00221 | 0.21191 | 3.8816 | 209.9585 | 0.04 | 2415 | 7175 | 7459 | 7754
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 14 | 11.32 | 150 | 0 | 80 | 11 | 0.00588 | 0.00225 | 0.00462 | 0.00386 | 0.00206 | 0.00323 | 0.0039 | 0.00428 | 0.00428 | 0.00258 | 0.003 | 0.003 | 0.15748 | 2.7579 | 176.29 | 0.04 | 4176 | 11335 | 11652 | 11978
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 15 | 11.65 | 150 | 0 | 80 | 11 | 0.00598 | 0.00196 | 0.00402 | 0.00393 | 0.00206 | 0.00329 | 0.00397 | 0.00372 | 0.00372 | 0.00262 | 0.00305 | 0.00305 | 0.15942 | 2.8586 | 181.0585 | 0.04 | 3916 | 10732 | 11043 | 11363
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 10 | 16 | 11.98 | 150 | 0 | 80 | 11 | 0.00608 | 0.00195 | 0.00353 | 0.00399 | 0.00206 | 0.00334 | 0.00404 | 0.00328 | 0.00328 | 0.00267 | 0.0031 | 0.0031 | 0.18112 | 3.1363 | 185.827 | 0.04 | 3453 | 9707 | 10017 | 10336
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 17.5 | 15.155 | 150 | 0 | 80 | 11 | 0.00324 | 0.00194 | 0.00336 | 0.00215 | 0.00198 | 0.00198 | 0.00217 | 0.00312 | 0.00312 | 0.00198 | 0.00198 | 0.00198 | 0.44186 | 6.2419 | 231.7057 | 0.04 | 1228 | 3895 | 4311 | 4588
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 18 | 15.32 | 150 | 0 | 80 | 11 | 0.00326 | 0.00193 | 0.00318 | 0.00216 | 0.00198 | 0.00198 | 0.00218 | 0.00295 | 0.00295 | 0.00198 | 0.00198 | 0.00198 | 0.45754 | 6.4228 | 234.09 | 0.04 | 1171 | 3605 | 4139 | 4413
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 19 | 15.65 | 150 | 0 | 80 | 11 | 0.00331 | 0.00193 | 0.00287 | 0.0022 | 0.00198 | 0.00198 | 0.00221 | 0.00266 | 0.00266 | 0.00198 | 0.00198 | 0.00198 | 0.48976 | 6.7921 | 238.8585 | 0.04 | 1066 | 3031 | 3814 | 4082
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 12 | 12 | 150 | 0 | 80 | 11 | 0.00398 | 0.00329 | 0.00683 | 0.00263 | 0.00201 | 0.00221 | 0.00265 | 0.00631 | 0.00631 | 0.00201 | 0.00205 | 0.00205 | 0.28145 | 3.9165 | 186.116 | 0.04 | 2694 | 8023 | 8344 | 8677
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 13 | 13 | 150 | 0 | 80 | 11 | 0.00347 | 0.00289 | 0.00595 | 0.0023 | 0.00199 | 0.00199 | 0.00232 | 0.00551 | 0.00551 | 0.00199 | 0.00199 | 0.00199 | 0.48719 | 5.5969 | 200.566 | 0.04 | 1629 | 5264 | 5568 | 5888
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 14 | 14 | 150 | 0 | 80 | 11 | 0.00308 | 0.00256 | 0.00527 | 0.00204 | 0.00198 | 0.00198 | 0.00206 | 0.00488 | 0.00488 | 0.00198 | 0.00198 | 0.00198 | 0.58463 | 6.6177 | 215.016 | 0.04 | 1225 | 3624 | 4359 | 4657
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 15 | 15 | 150 | 0 | 80 | 11 | 0.00276 | 0.0023 | 0.00472 | 0.00196 | 0.00196 | 0.00196 | 0.00196 | 0.00437 | 0.00437 | 0.00196 | 0.00196 | 0.00196 | 0.58379 | 7.0993 | 229.466 | 0.04 | 1045 | 2717 | 3727 | 4054
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 16 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.00208 | 0.00426 | 0.00195 | 0.00195 | 0.00195 | 0.00195 | 0.00394 | 0.00394 | 0.00195 | 0.00195 | 0.00195 | 0.58457 | 7.5908 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
| 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 17 | 17 | 150 | 0 | 80 | 11 | 0.00228 | 0.00194 | 0.00387 | 0.00194 | 0.00194 | 0.00194 | 0.00194 | 0.00358 | 0.00358 | 0.00194 | 0.00194 | 0.00194 | 0.58778 | 8.0998 | 258.366 | 0.04 | 774 | 1263 | 2336 | 3079