## Slab_Properties
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span
l2 = | 34 | ft | interior
l1 / l2 = | 1 |  | * must be < 2.0
c1 = | 32 | in
c2 = | 32 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 18 | in
d = | 16.75 | in
wc = | 150 | pcf
yt = | 9 | in
n = | 5.6374
lcw = | 1
fr = | 318.1981 | psi
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 225 | psf
mass = | 8472.5466 | lb sec2/ft
weight = | 272.816 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 398 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1660.6771 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1660.6771 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 863.5521 | k-ft
M1n1u = | 431.776 | k-ft
M1n2u = | 1162.474 | k-ft
M2pu = | 581.237 | k-ft
M2n1u = | 1079.4401 | k-ft
M2n2u = | 1079.4401 | k-ft
Service Moments
M01,DL = | 938.825 | k-ft | *includes SDL and self-weight
M01,LL = | 333.8044 | k-ft
M02,DL = | 938.825 | k-ft
M02,LL = | 333.8044 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 292.9134 | 195.2756 | k-ft
l1 | DL | n1 | 244.0945 | 0 | k-ft
l1 | DL | n2 | 492.8831 | 152.5591 | k-ft
l1 | LL | p | 104.147 | 69.4313 | k-ft
l1 | LL | n1 | 86.7892 | 0 | k-ft
l1 | LL | n2 | 175.2473 | 58.4158 | k-ft
l2 | DL | p | 197.1532 | 131.4355 | k-ft
l2 | DL | n1 | 457.6772 | 152.5591 | k-ft
l2 | DL | n2 | 457.6772 | 152.5591 | k-ft
l2 | LL | p | 70.0989 | 46.7326 | k-ft
l2 | LL | n1 | 162.7297 | 54.2432 | k-ft
l2 | LL | n2 | 162.7297 | 54.2432 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 518.1313 | 345.4208 | k-ft
l1 | n1 | 431.776 | 0 | k-ft
l1 | n2 | 871.8555 | 276.5361 | k-ft
l2 | p | 348.7422 | 232.4948 | k-ft
l2 | n1 | 809.5801 | 269.86 | k-ft
l2 | n2 | 809.5801 | 269.86 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation: |  |  |  |  | User input:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Column | Middle
l1 | p | 8.5425 | 8.5425 | in2 | l1 | p | 8.5425 | 8.5425 | in2
l1 | n1 | 8.5425 | 8.5425 | in2 | l1 | n1 | 8.5425 | 8.5425 | in2
l1 | n2 | 9.8319 | 8.5425 | in2 | l1 | n2 | 9.8319 | 8.5425 | in2
l2 | p | 8.5425 | 8.5425 | in2 | l2 | p | 8.5425 | 8.5425 | in2
l2 | n1 | 9.1296 | 8.5425 | in2 | l2 | n1 | 9.1296 | 8.5425 | in2
l2 | n2 | 9.1296 | 8.5425 | in2 | l2 | n2 | 9.1296 | 8.5425 | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 99144 | 99144 | in3
l1 | n1 | 99144 | 99144 | in3
l1 | n2 | 99144 | 99144 | in3
l2 | p | 99144 | 99144 | in3
l2 | n1 | 99144 | 99144 | in3
l2 | n2 | 99144 | 99144 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 20923.5793 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.73567 | 1.1035 | 0.03 | 0.03
l1 | n1 | 35434.0914 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.88281 | 1.1 | 0.03 | 0.03
l1 | n2 | 14747.5382 | 99144 | in3 | 3.6806 | 4.2361 | 2.7574 | 2.586 | 12277.7365 | 10837.3136 | 292.1058 | 292.1058 | 0.4372 | 1.3846 | 0.034528 | 0.03
l2 | p | 99144 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 1.093 | 1.6395 | 0.03 | 0.03
l2 | n1 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
l2 | n2 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 22173.75 | 99144 | in3
l2 | 73690.781 | 99144 | in3
Calculate Panel Ie
Iep = | 121317.75 | in3
Calculate Panel Ig
Igp = | 198288 | in3
Calculate k1
k1 = | 0.61183
Calculate fi |  |  | Interp li2
k2 = | 2.1 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 7.3292 | slug / ft2 | 2 | 9.29
fi = | 8.7619 | Hz
Calculate/Input Parameters for DG11
W = | 272816 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits
fn= | 8.7619 | Hz
W = | 272816 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips
Very Slow | 8.7619 | 1.25 | [5 empty] | 656.1208 |  | 656.1208 |  | 656.1208 | mips
Slow | 8.7619 | 1.6 | 6.8 | 6 | 8 | 0.1 | 2255.7196 | 1078.8285 | 3592.9892 | 1216.1941 | N/A | 1078.8285 | mips | * does not consider mode scaling
Moderate | 8.7619 | 1.85 | 8 | 7 | 9 | 0.09 | 2462.2805 | 1429.2044 | 3228.1498 | 1380.8096 | 1600.7426 | 1600.7426 | mips
Fast | 8.7619 | 2.1 | 8.8 | 8 | 10 | 0.08 | 2687.7567 | 1815.3443 | 2989.6115 | 1537.3001 | 2436.3591 | 2436.3591 | mips

## Sample_Slabs
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.26404 | 3.43 | 186.116 | 0.04 | 3130 | 9008 | 9322 | 9647
2 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.2769 | 3.88 | 186.116 | 0.04 | 2725 | 8097 | 8417 | 8750
3 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.29152 | 3.99 | 186.116 | 0.04 | 2640 | 7897 | 8218 | 8553
4 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.3093 | 4.11 | 186.116 | 0.04 | 2551 | 7688 | 8011 | 8347
5 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.33328 | 4.26 | 186.116 | 0.04 | 2447 | 7439 | 7763 | 8101
6 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.01 | 200.566 | 0.04 | 1871 | 5904 | 6207 | 6526
7 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47936 | 5.55 | 200.566 | 0.04 | 1648 | 5315 | 5618 | 5938
8 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48247 | 5.57 | 200.566 | 0.04 | 1640 | 5294 | 5598 | 5918
9 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.48586 | 5.59 | 200.566 | 0.04 | 1633 | 5274 | 5578 | 5898
10 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.4902 | 5.61 | 200.566 | 0.04 | 1626 | 5254 | 5558 | 5878
11 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.47671 | 5.01 | 200.566 | 0.04 | 1871 | 5904 | 6207 | 6526
12 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.47936 | 5.55 | 200.566 | 0.04 | 1648 | 5315 | 5618 | 5938
13 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.48247 | 5.57 | 200.566 | 0.04 | 1640 | 5294 | 5598 | 5918
14 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57362 | 6.56 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
15 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.5736 | 6.55 | 215.016 | 0.04 | 1242 | 3730 | 4410 | 4708
16 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.53456 | 5.73 | 215.016 | 0.04 | 1477 | 4793 | 5076 | 5375
17 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.5514 | 6.43 | 215.016 | 0.04 | 1273 | 3911 | 4499 | 4798
18 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.57369 | 6.56 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
19 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.57362 | 6.56 | 215.016 | 0.04 | 1240 | 3715 | 4402 | 4701
20 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.5736 | 6.55 | 215.016 | 0.04 | 1242 | 3730 | 4410 | 4708
21 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.57675 | 6.38 | 229.466 | 0.04 | 1205 | 3734 | 4250 | 4530
22 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.57726 | 7.06 | 229.466 | 0.04 | 1053 | 2774 | 3771 | 4079
23 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.57782 | 7.06 | 229.466 | 0.04 | 1053 | 2774 | 3771 | 4079
24 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.5784 | 7.07 | 229.466 | 0.04 | 1051 | 2760 | 3760 | 4072
25 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.57902 | 7.07 | 229.466 | 0.04 | 1051 | 2760 | 3760 | 4072
26 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.58291 | 6.86 | 243.916 | 0.04 | 1030 | 2876 | 3694 | 3956
27 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.58371 | 7.59 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
28 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.58456 | 7.59 | 243.916 | 0.04 | 898 | 1905 | 3002 | 3548
29 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.58545 | 7.6 | 243.916 | 0.04 | 896 | 1892 | 2991 | 3542
30 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.58641 | 7.6 | 243.916 | 0.04 | 896 | 1892 | 2991 | 3542
31 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.59118 | 7.35 | 258.366 | 0.04 | 886 | 2099 | 3067 | 3469
32 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.59241 | 8.13 | 258.366 | 0.04 | 770 | 1257 | 2306 | 3056
33 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.5937 | 8.14 | 258.366 | 0.04 | 769 | 1255 | 2296 | 3049
34 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.59512 | 8.15 | 258.366 | 0.04 | 768 | 1253 | 2287 | 3041
35 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.59668 | 8.16 | 258.366 | 0.04 | 766 | 1251 | 2277 | 3033
36 | 34 | 34 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.60273 | 7.87 | 272.816 | 0.04 | 764 | 1371 | 2425 | 3046
37 | 34 | 34 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.60472 | 8.71 | 272.816 | 0.04 | 662 | 1087 | 1649 | 2474
38 | 34 | 34 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.60687 | 8.73 | 272.816 | 0.04 | 660 | 1084 | 1630 | 2460
39 | 34 | 34 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.60923 | 8.74 | 272.816 | 0.04 | 659 | 1082 | 1621 | 2452
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.61182 | 8.76 | 272.816 | 0.04 | 656 | 1079 | 1603 | 2438

## SSM_Example
Slab properties: |  |  | bay type
l1 = | 35 | ft | exterior | * must be larger span
l2 = | 22 | ft | interior
l1 / l2 = | 1.5909 |  | * must be < 2.0
c1 = | 21 | in
c2 = | 21 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 4889136.8257 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 11 | in
d = | 9.75 | in
wc = | 145 | pcf
yt = | 5.5 | in
n = | 5.9315
lcw = | 0.85
fr = | 270.4683 | psi
Strip widths
Direction | Column | Middle
l1 | 11 | 11 | ft | * needs to be adjusted for exterior spans?
l2 | 11 | 24 | ft
Loading
SDL = | 21 | psf
LL = | 125 | psf
LLvib = | 11 | psf
Self weight = | 132.9167 | psf
mass = | 3943.6594 | lb sec2/ft
weight = | 126.9858 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 384.7 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1169.6022 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 690.1608 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 608.1931 | k-ft
M1n1u = | 304.0966 | k-ft
M1n2u = | 818.7215 | k-ft
M2pu = | 241.5563 | k-ft
M2n1u = | 448.6045 | k-ft
M2n2u = | 448.6045 | k-ft
Service Moments
M01,DL = | 467.9524 | k-ft
M01,LL = | 380.0371 | k-ft
M02,DL = | 276.1301 | k-ft
M02,LL = | 224.2529 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 146.0011 | 97.3341 | k-ft
l1 | DL | n1 | 121.6676 | 0 | k-ft
l1 | DL | n2 | 245.675 | 76.0423 | k-ft
l1 | LL | p | 118.5716 | 79.0477 | k-ft
l1 | LL | n1 | 98.8096 | 0 | k-ft
l1 | LL | n2 | 199.5195 | 66.5065 | k-ft
l2 | DL | p | 57.9873 | 38.6582 | k-ft
l2 | DL | n1 | 134.6134 | 44.8711 | k-ft
l2 | DL | n2 | 134.6134 | 44.8711 | k-ft
l2 | LL | p | 47.0931 | 31.3954 | k-ft
l2 | LL | n1 | 109.3233 | 36.4411 | k-ft
l2 | LL | n2 | 109.3233 | 36.4411 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 364.9159 | 243.2773 | k-ft
l1 | n1 | 304.0966 | 0 | k-ft
l1 | n2 | 614.0412 | 197.6611 | k-ft
l2 | p | 144.9338 | 96.6225 | k-ft
l2 | n1 | 336.4534 | 112.1511 | k-ft
l2 | n2 | 336.4534 | 112.1511 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | User input:
l1 | p | 7.0696 | 4.7131 | in2 | l1 | p | 7.0696 | 4.7131 | in2
l1 | n1 | 5.8913 | 3.2175 | in2 | l1 | n1 | 5.8913 | 3.2175 | in2
l1 | n2 | 11.896 | 3.8293 | in2 | l1 | n2 | 11.896 | 3.8293 | in2
l2 | p | 3.2175 | 7.02 | in2 | l2 | p | 3.2175 | 7.02 | in2
l2 | n1 | 6.5182 | 7.02 | in2 | l2 | n1 | 6.5182 | 7.02 | in2
l2 | n2 | 6.5182 | 7.02 | in2 | l2 | n2 | 6.5182 | 7.02 | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 14641 | 14641 | in3
l1 | n1 | 14641 | 14641 | in3
l1 | n2 | 14641 | 14641 | in3
l2 | p | 14641 | 31944 | in3
l2 | n1 | 14641 | 31944 | in3
l2 | n2 | 14641 | 31944 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 2982.2197 | 2247.3153 | in3 | 3.1478 | 4.7218 | 2.1914 | 1.8314 | 2858.7979 | 2023.2082 | 59.9989 | 59.9989 | 0.22678 | 0.34016 | 0.065917 | 0.043945
l1 | n1 | 2611.7399 | 14641 | in3 | 3.7774 | 6.9166 | 2.0227 | 1.5407 | 2450.7004 | 1447.0836 | 59.9989 | 59.9989 | 0.27213 | 1.1 | 0.054931 | 0.03
l1 | n2 | 4428.9103 | 2001.5362 | in3 | 1.8707 | 5.8115 | 2.738 | 1.6678 | 4372.492 | 1687.826 | 59.9989 | 59.9989 | 0.13477 | 0.4209 | 0.11092 | 0.035705
l2 | p | 2049.1012 | 31944 | in3 | 6.9166 | 6.9166 | 1.5407 | 1.5407 | 1447.0836 | 3157.2734 | 59.9989 | 130.9067 | 0.57098 | 1.8687 | 0.03 | 0.03
l2 | n1 | 2808.998 | 31944 | in3 | 3.4141 | 6.9166 | 2.1149 | 1.5407 | 2670.0536 | 3157.2734 | 59.9989 | 130.9067 | 0.24596 | 1.6099 | 0.060776 | 0.03
l2 | n2 | 2808.998 | 31944 | in3 | 3.4141 | 6.9166 | 2.1149 | 1.5407 | 2670.0536 | 3157.2734 | 59.9989 | 130.9067 | 0.24596 | 1.6099 | 0.060776 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 3143.6513 | 4069.5011 | in3
l2 | 2277.0702 | 31944 | in3
Calculate Panel Ie
Iep = | 20717.1113 | in3
Calculate Panel Ig
Igp = | 37933.5 | in3
Calculate k1
k1 = | 0.54614
Calculate fi |  |  | Interp li2
k2 = | 1.9 |  | 1 | 7.12
li2 = | 8.9873 |  | 1.5 | 8.92
g = | 5.1216 | slug / ft2 | 2 | 9.29
fi = | 4.9705 | Hz
Calculate/Input Parameters for DG11
W = | 126985.8333 | lb
b = | 0.03