## Slab_Properties
Slab properties: |  |  | bay type
l1 = | 34 | ft | exterior | * must be larger span
l2 = | 34 | ft | interior
l1 / l2 = | 1 |  | * must be < 2.0
c1 = | 32 | in
c2 = | 32 | in
ν = | 0.2
f'c = | 5000 | psi
fy = | 60000 | psi
Ec = | 5144190.8985 | psi | *1.2 Multiplier due to Dynamic effects (stiffer)
h = | 18 | in
d = | 16.75 | in
wc = | 150 | pcf
yt = | 9 | in
n = | 5.6374
lcw = | 1
fr = | 318.1981 | psi
Strip widths
Direction | Column | Middle
l1 | 17 | 17 | ft | * needs to be adjusted for exterior spans?
l2 | 17 | 17 | ft
Loading
SDL = | 0 | psf
LL = | 80 | psf
LLvib = | 11 | psf
Self weight = | 225 | psf
mass = | 8472.5466 | lb sec2/ft
weight = | 272.816 | kips
Direct Design Method (must fulfill ACI 318-14 8.10.2) |  |  |  |  | Moment Distribution Coefficients
[5 empty] | Interior Bay | Interior Bay | Interior Bay | Interior Bay | Exterior Bay | Exterior Bay | Exterior Bay | Exterior Bay
Static Moment, M0 |  |  |  |  | Column | Column | Middle | Middle | Column | Column | Middle | Middle
qu = | 398 |  |  | location | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor | % To Strip | Dist Factor
M01u = | 1660.6771 | k-ft |  | positive, p | 0.35 | 0.6 | 0.35 | 0.4 | 0.52 | 0.6 | 0.52 | 0.4
M02u = | 1660.6771 | k-ft |  | negative exterior*, n1 | 0.65 | 0.75 | 0.65 | 0.25 | 0.26 | 1 | 0.26 | 0 | * for interior span, negative moments are the same
|  |  |  | negative interior, n2 | 0.65 | 0.75 | 0.65 | 0.25 | 0.7 | 0.75 | 0.7 | 0.25
M1pu = | 863.5521 | k-ft
M1n1u = | 431.776 | k-ft
M1n2u = | 1162.474 | k-ft
M2pu = | 581.237 | k-ft
M2n1u = | 1079.4401 | k-ft
M2n2u = | 1079.4401 | k-ft
Service Moments
M01,DL = | 938.825 | k-ft | *includes SDL and self-weight
M01,LL = | 333.8044 | k-ft
M02,DL = | 938.825 | k-ft
M02,LL = | 333.8044 | k-ft
Calculate Service Strip Ma
Direction | Type | Location | Column | Middle
l1 | DL | p | 292.9134 | 195.2756 | k-ft
l1 | DL | n1 | 244.0945 | 0 | k-ft
l1 | DL | n2 | 492.8831 | 152.5591 | k-ft
l1 | LL | p | 104.147 | 69.4313 | k-ft
l1 | LL | n1 | 86.7892 | 0 | k-ft
l1 | LL | n2 | 175.2473 | 58.4158 | k-ft
l2 | DL | p | 197.1532 | 131.4355 | k-ft
l2 | DL | n1 | 457.6772 | 152.5591 | k-ft
l2 | DL | n2 | 457.6772 | 152.5591 | k-ft
l2 | LL | p | 70.0989 | 46.7326 | k-ft
l2 | LL | n1 | 162.7297 | 54.2432 | k-ft
l2 | LL | n2 | 162.7297 | 54.2432 | k-ft
Calculate Factored Strip Mu
Direction | Location | Column | Middle
l1 | p | 518.1313 | 345.4208 | k-ft
l1 | n1 | 431.776 | 0 | k-ft
l1 | n2 | 871.8555 | 276.5361 | k-ft
l2 | p | 348.7422 | 232.4948 | k-ft
l2 | n1 | 809.5801 | 269.86 | k-ft
l2 | n2 | 809.5801 | 269.86 | k-ft
Input/Calculate flexural reinforcement, As |  |  |  |  | SSM Estimation: |  |  |  |  | User input:
Direction | Location | Column | Middle |  | Direction | Location | Column | Middle |  | Column | Middle
l1 | p | 8.5425 | 8.5425 | in2 | l1 | p | 8.5425 | 8.5425 | in2
l1 | n1 | 8.5425 | 8.5425 | in2 | l1 | n1 | 8.5425 | 8.5425 | in2
l1 | n2 | 9.8319 | 8.5425 | in2 | l1 | n2 | 9.8319 | 8.5425 | in2
l2 | p | 8.5425 | 8.5425 | in2 | l2 | p | 8.5425 | 8.5425 | in2
l2 | n1 | 9.1296 | 8.5425 | in2 | l2 | n1 | 9.1296 | 8.5425 | in2
l2 | n2 | 9.1296 | 8.5425 | in2 | l2 | n2 | 9.1296 | 8.5425 | in2
Calculate strip Ig
Direction | Location | Column | Middle
l1 | p | 99144 | 99144 | in3
l1 | n1 | 99144 | 99144 | in3
l1 | n2 | 99144 | 99144 | in3
l2 | p | 99144 | 99144 | in3
l2 | n1 | 99144 | 99144 | in3
l2 | n2 | 99144 | 99144 | in3
[5 empty] | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle | Column | Middle
Calculate strips Ie |  |  |  |  | aj | aj | kd | kd | Icr | Icr | Mcr | Mcr | Mcr/Ma | Mcr/Ma | r | r
Direction | Location | Column | Middle |  | in2 | in2 | in | in | in3 | in3 | k-ft | k-ft
l1 | p | 20923.5793 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.73567 | 1.1035 | 0.03 | 0.03
l1 | n1 | 35434.0914 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 0.88281 | 1.1 | 0.03 | 0.03
l1 | n2 | 14747.5382 | 99144 | in3 | 3.6806 | 4.2361 | 2.7574 | 2.586 | 12277.7365 | 10837.3136 | 292.1058 | 292.1058 | 0.4372 | 1.3846 | 0.034528 | 0.03
l2 | p | 99144 | 99144 | in3 | 4.2361 | 4.2361 | 2.586 | 2.586 | 10837.3136 | 10837.3136 | 292.1058 | 292.1058 | 1.093 | 1.6395 | 0.03 | 0.03
l2 | n1 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
l2 | n2 | 14299.9366 | 99144 | in3 | 3.9637 | 4.2361 | 2.6658 | 2.586 | 11497.5421 | 10837.3136 | 292.1058 | 292.1058 | 0.47083 | 1.4125 | 0.032062 | 0.03
Calculate avg strip Ie
Direction | Column | Middle
l1 | 22173.75 | 99144 | in3
l2 | 73690.781 | 99144 | in3
Calculate Panel Ie
Iep = | 121317.75 | in3
Calculate Panel Ig
Igp = | 198288 | in3
Calculate k1
k1 = | 0.61183
Calculate fi |  |  | Interp li2
k2 = | 2.1 |  | 1 | 7.12
li2 = | 7.12 |  | 1.5 | 8.92
g = | 7.3292 | slug / ft2 | 2 | 9.29
fi = | 8.7619 | Hz
Calculate/Input Parameters for DG11
W = | 272816 | lb
b = | 0.04

## AISC_DG_11_Sensitive_Equipment
6.1.4 Generic Velocity Limits
fn= | 8.7619 | Hz
W = | 272816 | lb
b = | 0.04
Table 6-1. Walking Parameters | [6 empty] | 6-3b (1) | 6-3b (2) |  |  | Interpolated
Speed | fn | fstep | f4max | fL | fU | g | fn <= fL | fn >= fU | fn = fL | fn = fU | fL < fn < fU
| Hz | Hz | Hz | Hz | Hz |  | mips | mips | mips | mips | mips
Very Slow | 8.7619 | 1.25 | [5 empty] | 656.1208 |  | 656.1208 |  | 656.1208 | mips
Slow | 8.7619 | 1.6 | 6.8 | 6 | 8 | 0.1 | 2255.7196 | 1078.8285 | 3592.9892 | 1216.1941 | N/A | 1078.8285 | mips | * does not consider mode scaling
Moderate | 8.7619 | 1.85 | 8 | 7 | 9 | 0.09 | 2462.2805 | 1429.2044 | 3228.1498 | 1380.8096 | 1600.7426 | 1600.7426 | mips
Fast | 8.7619 | 2.1 | 8.8 | 8 | 10 | 0.08 | 2687.7567 | 1815.3443 | 2989.6115 | 1537.3001 | 2436.3591 | 2436.3591 | mips

## Rho_default
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00335 | 0.00279 | 0.00564 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00523 | 0.00523 | 0.0025 | 0.0025 | 0.0025 | 0.43135 | 4.1601 | 185.472 | 0.03 | 2767 | 10171 | 10603 | 11053
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00332 | 0.00276 | 0.00558 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00518 | 0.00518 | 0.0025 | 0.0025 | 0.0025 | 0.43159 | 4.5993 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00328 | 0.00274 | 0.00552 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00513 | 0.00513 | 0.0025 | 0.0025 | 0.0025 | 0.43184 | 4.6006 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00325 | 0.0027 | 0.00546 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00508 | 0.00508 | 0.0025 | 0.0025 | 0.0025 | 0.43214 | 4.6023 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00321 | 0.00268 | 0.0054 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00502 | 0.00502 | 0.0025 | 0.0025 | 0.0025 | 0.43241 | 4.6037 | 185.472 | 0.03 | 2479 | 9256 | 9692 | 10148
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.43708 | 4.5486 | 199.872 | 0.03 | 2328 | 8679 | 9084 | 9506
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.43772 | 5.0311 | 199.872 | 0.03 | 2081 | 7868 | 8274 | 8701
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.43845 | 5.0353 | 199.872 | 0.03 | 2076 | 7852 | 8258 | 8685
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00285 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00446 | 0.00446 | 0.0025 | 0.0025 | 0.0025 | 0.43926 | 5.0399 | 199.872 | 0.03 | 2076 | 7852 | 8258 | 8685
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00282 | 0.0025 | 0.00474 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.4401 | 5.0447 | 199.872 | 0.03 | 2076 | 7852 | 8258 | 8685
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00294 | 0.0025 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0046 | 0.0046 | 0.0025 | 0.0025 | 0.0025 | 0.43708 | 4.5486 | 199.872 | 0.03 | 2328 | 8679 | 9084 | 9506
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00291 | 0.0025 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00455 | 0.00455 | 0.0025 | 0.0025 | 0.0025 | 0.43772 | 5.0311 | 199.872 | 0.03 | 2081 | 7868 | 8274 | 8701
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00288 | 0.0025 | 0.00485 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.43845 | 5.0353 | 199.872 | 0.03 | 2076 | 7852 | 8258 | 8685
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.45206 | 5.5187 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.45394 | 5.5301 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00261 | 0.0025 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00408 | 0.00408 | 0.0025 | 0.0025 | 0.0025 | 0.44753 | 4.968 | 214.272 | 0.03 | 1968 | 7428 | 7807 | 8204
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00259 | 0.0025 | 0.00435 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00404 | 0.00404 | 0.0025 | 0.0025 | 0.0025 | 0.44891 | 5.4994 | 214.272 | 0.03 | 1753 | 6697 | 7075 | 7475
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00256 | 0.0025 | 0.00431 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.45048 | 5.509 | 214.272 | 0.03 | 1749 | 6684 | 7062 | 7462
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00253 | 0.0025 | 0.00426 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00396 | 0.00396 | 0.0025 | 0.0025 | 0.0025 | 0.45206 | 5.5187 | 214.272 | 0.03 | 1745 | 6671 | 7050 | 7450
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00251 | 0.0025 | 0.00422 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00392 | 0.00392 | 0.0025 | 0.0025 | 0.0025 | 0.45394 | 5.5301 | 214.272 | 0.03 | 1742 | 6658 | 7037 | 7437
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00395 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00367 | 0.00367 | 0.0025 | 0.0025 | 0.0025 | 0.46717 | 5.4491 | 228.672 | 0.03 | 1660 | 6335 | 6690 | 7065
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00391 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00363 | 0.00363 | 0.0025 | 0.0025 | 0.0025 | 0.47029 | 6.0428 | 228.672 | 0.03 | 1471 | 5634 | 6026 | 6401
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00387 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00359 | 0.00359 | 0.0025 | 0.0025 | 0.0025 | 0.47388 | 6.0658 | 228.672 | 0.03 | 1463 | 5573 | 5995 | 6370
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00383 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00355 | 0.00355 | 0.0025 | 0.0025 | 0.0025 | 0.47772 | 6.0903 | 228.672 | 0.03 | 1457 | 5532 | 5975 | 6350
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00379 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00352 | 0.00352 | 0.0025 | 0.0025 | 0.0025 | 0.48217 | 6.1187 | 228.672 | 0.03 | 1449 | 5471 | 5944 | 6319
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00358 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00332 | 0.00332 | 0.0025 | 0.0025 | 0.0025 | 0.507 | 6.0656 | 243.072 | 0.03 | 1376 | 5242 | 5640 | 5993
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00354 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00329 | 0.00329 | 0.0025 | 0.0025 | 0.0025 | 0.51503 | 6.757 | 243.072 | 0.03 | 1208 | 3923 | 5023 | 5374
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0035 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00325 | 0.00325 | 0.0025 | 0.0025 | 0.0025 | 0.52495 | 6.8218 | 243.072 | 0.03 | 1195 | 3809 | 4974 | 5325
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00347 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00322 | 0.00322 | 0.0025 | 0.0025 | 0.0025 | 0.53669 | 6.8977 | 243.072 | 0.03 | 1178 | 3656 | 4909 | 5260
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00343 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00319 | 0.00319 | 0.0025 | 0.0025 | 0.0025 | 0.55153 | 6.9924 | 243.072 | 0.03 | 1160 | 3484 | 4838 | 5188
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00327 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00303 | 0.00303 | 0.0025 | 0.0025 | 0.0025 | 0.60209 | 7.0339 | 257.472 | 0.03 | 1087 | 3217 | 4516 | 4869
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00323 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.62728 | 7.9353 | 257.472 | 0.03 | 933 | 1574 | 3197 | 4260
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0032 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00297 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.63844 | 8.0056 | 257.472 | 0.03 | 922 | 1464 | 3096 | 4211
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00317 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00294 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.64174 | 8.0263 | 257.472 | 0.03 | 919 | 1459 | 3067 | 4187
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00313 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00291 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.64545 | 8.0495 | 257.472 | 0.03 | 916 | 1455 | 3037 | 4164
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00279 | 0.00279 | 0.0025 | 0.0025 | 0.0025 | 0.66311 | 7.8267 | 271.872 | 0.03 | 899 | 1679 | 3179 | 4098
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00297 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00276 | 0.00276 | 0.0025 | 0.0025 | 0.0025 | 0.6697 | 8.6934 | 271.872 | 0.03 | 786 | 1256 | 1998 | 3222
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00294 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00273 | 0.00273 | 0.0025 | 0.0025 | 0.0025 | 0.67783 | 8.7461 | 271.872 | 0.03 | 778 | 1245 | 1915 | 3155
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00291 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0027 | 0.0027 | 0.0025 | 0.0025 | 0.0025 | 0.68742 | 8.8077 | 271.872 | 0.03 | 771 | 1235 | 1833 | 3087
40 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00288 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00267 | 0.00267 | 0.0025 | 0.0025 | 0.0025 | 0.69931 | 8.8836 | 271.872 | 0.03 | 763 | 1223 | 1737 | 3008

## Rho_25%nonmin
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0041875 | 0.0034875 | 0.00705 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0065375 | 0.0065375 | 0.0025 | 0.0025 | 0.0025 | 0.44151 | 4.2088 | 185.472 | 0.03 | 2731 | 10060 | 10492 | 10944
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00415 | 0.00345 | 0.006975 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006475 | 0.006475 | 0.0025 | 0.0025 | 0.0025 | 0.44169 | 4.6528 | 185.472 | 0.03 | 2449 | 9160 | 9596 | 10053
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0041 | 0.003425 | 0.0069 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0064125 | 0.0064125 | 0.0025 | 0.0025 | 0.0025 | 0.44187 | 4.6538 | 185.472 | 0.03 | 2449 | 9160 | 9596 | 10053
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0040625 | 0.003375 | 0.006825 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00635 | 0.00635 | 0.0025 | 0.0025 | 0.0025 | 0.44212 | 4.6551 | 185.472 | 0.03 | 2443 | 9141 | 9577 | 10034
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0040125 | 0.00335 | 0.00675 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006275 | 0.006275 | 0.0025 | 0.0025 | 0.0025 | 0.44232 | 4.6562 | 185.472 | 0.03 | 2443 | 9141 | 9577 | 10034
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003675 | 0.0025 | 0.0061875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00575 | 0.00575 | 0.0025 | 0.0025 | 0.0025 | 0.44581 | 4.5938 | 199.872 | 0.03 | 2306 | 8607 | 9011 | 9435
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036375 | 0.0025 | 0.006125 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0056875 | 0.0056875 | 0.0025 | 0.0025 | 0.0025 | 0.44639 | 5.0807 | 199.872 | 0.03 | 2058 | 7790 | 8196 | 8623
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036 | 0.0025 | 0.0060625 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005625 | 0.005625 | 0.0025 | 0.0025 | 0.0025 | 0.44707 | 5.0846 | 199.872 | 0.03 | 2058 | 7790 | 8196 | 8623
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0035625 | 0.0025 | 0.006 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005575 | 0.005575 | 0.0025 | 0.0025 | 0.0025 | 0.44783 | 5.0889 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003525 | 0.0025 | 0.005925 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0055125 | 0.0055125 | 0.0025 | 0.0025 | 0.0025 | 0.44862 | 5.0934 | 199.872 | 0.03 | 2053 | 7775 | 8181 | 8608
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003675 | 0.0025 | 0.0061875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00575 | 0.00575 | 0.0025 | 0.0025 | 0.0025 | 0.44581 | 4.5938 | 199.872 | 0.03 | 2306 | 8607 | 9011 | 9435
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036375 | 0.0025 | 0.006125 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0056875 | 0.0056875 | 0.0025 | 0.0025 | 0.0025 | 0.44639 | 5.0807 | 199.872 | 0.03 | 2058 | 7790 | 8196 | 8623
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036 | 0.0025 | 0.0060625 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005625 | 0.005625 | 0.0025 | 0.0025 | 0.0025 | 0.44707 | 5.0846 | 199.872 | 0.03 | 2058 | 7790 | 8196 | 8623
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031625 | 0.0025 | 0.005325 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00495 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.46027 | 5.5686 | 214.272 | 0.03 | 1727 | 6608 | 6986 | 7387
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031375 | 0.0025 | 0.005275 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0049 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.46212 | 5.5797 | 214.272 | 0.03 | 1723 | 6595 | 6974 | 7374
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032625 | 0.0025 | 0.0055 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0051 | 0.0051 | 0.0025 | 0.0025 | 0.0025 | 0.45586 | 5.014 | 214.272 | 0.03 | 1950 | 7369 | 7747 | 8145
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032375 | 0.0025 | 0.0054375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00505 | 0.00505 | 0.0025 | 0.0025 | 0.0025 | 0.45721 | 5.55 | 214.272 | 0.03 | 1734 | 6633 | 7012 | 7412
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032 | 0.0025 | 0.0053875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005 | 0.005 | 0.0025 | 0.0025 | 0.0025 | 0.45873 | 5.5592 | 214.272 | 0.03 | 1731 | 6620 | 6999 | 7399
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031625 | 0.0025 | 0.005325 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00495 | 0.00495 | 0.0025 | 0.0025 | 0.0025 | 0.46027 | 5.5686 | 214.272 | 0.03 | 1727 | 6608 | 6986 | 7387
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031375 | 0.0025 | 0.005275 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0049 | 0.0049 | 0.0025 | 0.0025 | 0.0025 | 0.46212 | 5.5797 | 214.272 | 0.03 | 1723 | 6595 | 6974 | 7374
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0049375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045875 | 0.0045875 | 0.0025 | 0.0025 | 0.0025 | 0.47081 | 5.4703 | 228.672 | 0.03 | 1653 | 6311 | 6666 | 7041
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0048875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045375 | 0.0045375 | 0.0025 | 0.0025 | 0.0025 | 0.47391 | 6.066 | 228.672 | 0.03 | 1463 | 5573 | 5995 | 6370
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0048375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0044875 | 0.0044875 | 0.0025 | 0.0025 | 0.0025 | 0.47747 | 6.0888 | 228.672 | 0.03 | 1457 | 5532 | 5975 | 6350
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0047875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0044375 | 0.0044375 | 0.0025 | 0.0025 | 0.0025 | 0.48129 | 6.1131 | 228.672 | 0.03 | 1451 | 5491 | 5954 | 6329
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0047375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0044 | 0.0044 | 0.0025 | 0.0025 | 0.0025 | 0.48572 | 6.1412 | 228.672 | 0.03 | 1443 | 5430 | 5923 | 6299
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004475 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00415 | 0.00415 | 0.0025 | 0.0025 | 0.0025 | 0.51048 | 6.0864 | 243.072 | 0.03 | 1371 | 5204 | 5621 | 5974
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004425 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0041125 | 0.0041125 | 0.0025 | 0.0025 | 0.0025 | 0.51849 | 6.7797 | 243.072 | 0.03 | 1204 | 3885 | 5006 | 5357
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0040625 | 0.0040625 | 0.0025 | 0.0025 | 0.0025 | 0.5284 | 6.8441 | 243.072 | 0.03 | 1191 | 3770 | 4957 | 5308
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0043375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004025 | 0.004025 | 0.0025 | 0.0025 | 0.0025 | 0.54012 | 6.9197 | 243.072 | 0.03 | 1174 | 3617 | 4893 | 5244
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0042875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0039875 | 0.0039875 | 0.0025 | 0.0025 | 0.0025 | 0.55494 | 7.014 | 243.072 | 0.03 | 1156 | 3445 | 4815 | 5173
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0040875 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0037875 | 0.0037875 | 0.0025 | 0.0025 | 0.0025 | 0.60545 | 7.0535 | 257.472 | 0.03 | 1083 | 3181 | 4488 | 4854
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0040375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00375 | 0.00375 | 0.0025 | 0.0025 | 0.0025 | 0.63062 | 7.9564 | 257.472 | 0.03 | 930 | 1538 | 3168 | 4247
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0037125 | 0.0037125 | 0.0025 | 0.0025 | 0.0025 | 0.64177 | 8.0264 | 257.472 | 0.03 | 919 | 1459 | 3067 | 4187
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0039625 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003675 | 0.003675 | 0.0025 | 0.0025 | 0.0025 | 0.64505 | 8.047 | 257.472 | 0.03 | 916 | 1455 | 3037 | 4164
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0039125 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0036375 | 0.0036375 | 0.0025 | 0.0025 | 0.0025 | 0.64875 | 8.07 | 257.472 | 0.03 | 913 | 1451 | 3008 | 4140
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0034875 | 0.0034875 | 0.0025 | 0.0025 | 0.0025 | 0.66637 | 7.8459 | 271.872 | 0.03 | 896 | 1644 | 3152 | 4086
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0037125 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00345 | 0.00345 | 0.0025 | 0.0025 | 0.0025 | 0.67294 | 8.7145 | 271.872 | 0.03 | 783 | 1252 | 1970 | 3200
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.003675 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0034125 | 0.0034125 | 0.0025 | 0.0025 | 0.0025 | 0.68106 | 8.7669 | 271.872 | 0.03 | 776 | 1242 | 1888 | 3132
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0036375 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.003375 | 0.003375 | 0.0025 | 0.0025 | 0.0025 | 0.69063 | 8.8283 | 271.872 | 0.03 | 769 | 1231 | 1805 | 3065
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0036 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0033375 | 0.0033375 | 0.0025 | 0.0025 | 0.0025 | 0.61418 | 8.7788 | 272.816 | 0.03 | 772 | 1236 | 1867 | 3110

## Rho_50%nonmin
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.005025 | 0.004185 | 0.00846 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.007845 | 0.007845 | 0.0025 | 0.0025 | 0.0025 | 0.45112 | 4.2544 | 185.472 | 0.03 | 2703 | 9972 | 10405 | 10857
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00414 | 0.00837 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00777 | 0.00777 | 0.0025 | 0.0025 | 0.0025 | 0.45125 | 4.7029 | 185.472 | 0.03 | 2420 | 9066 | 9502 | 9959
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00411 | 0.00828 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.007695 | 0.007695 | 0.0025 | 0.0025 | 0.0025 | 0.45138 | 4.7036 | 185.472 | 0.03 | 2420 | 9066 | 9502 | 9959
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.004875 | 0.00405 | 0.00819 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00762 | 0.00762 | 0.0025 | 0.0025 | 0.0025 | 0.45157 | 4.7046 | 185.472 | 0.03 | 2420 | 9066 | 9502 | 9959
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.004815 | 0.00402 | 0.0081 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00753 | 0.00753 | 0.0025 | 0.0025 | 0.0025 | 0.45172 | 4.7054 | 185.472 | 0.03 | 2414 | 9047 | 9483 | 9941
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.0025 | 0.007425 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0069 | 0.0069 | 0.0025 | 0.0025 | 0.0025 | 0.45407 | 4.6362 | 199.872 | 0.03 | 2278 | 8518 | 8922 | 9346
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004365 | 0.0025 | 0.00735 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006825 | 0.006825 | 0.0025 | 0.0025 | 0.0025 | 0.45461 | 5.1272 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.0025 | 0.007275 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00675 | 0.00675 | 0.0025 | 0.0025 | 0.0025 | 0.45525 | 5.1308 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004275 | 0.0025 | 0.0072 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00669 | 0.00669 | 0.0025 | 0.0025 | 0.0025 | 0.45597 | 5.1349 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00423 | 0.0025 | 0.00711 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006615 | 0.006615 | 0.0025 | 0.0025 | 0.0025 | 0.45671 | 5.1391 | 199.872 | 0.03 | 2031 | 7698 | 8104 | 8532
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.0025 | 0.007425 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0069 | 0.0069 | 0.0025 | 0.0025 | 0.0025 | 0.45407 | 4.6362 | 199.872 | 0.03 | 2278 | 8518 | 8922 | 9346
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004365 | 0.0025 | 0.00735 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006825 | 0.006825 | 0.0025 | 0.0025 | 0.0025 | 0.45461 | 5.1272 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.0025 | 0.007275 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00675 | 0.00675 | 0.0025 | 0.0025 | 0.0025 | 0.45525 | 5.1308 | 199.872 | 0.03 | 2035 | 7714 | 8120 | 8547
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003795 | 0.0025 | 0.00639 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00594 | 0.00594 | 0.0025 | 0.0025 | 0.0025 | 0.46807 | 5.6155 | 214.272 | 0.03 | 1709 | 6546 | 6924 | 7324
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003765 | 0.0025 | 0.00633 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00588 | 0.00588 | 0.0025 | 0.0025 | 0.0025 | 0.46988 | 5.6264 | 214.272 | 0.03 | 1706 | 6533 | 6912 | 7312
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003915 | 0.0025 | 0.0066 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00612 | 0.00612 | 0.0025 | 0.0025 | 0.0025 | 0.46377 | 5.0573 | 214.272 | 0.03 | 1928 | 7296 | 7674 | 8073
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003885 | 0.0025 | 0.006525 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00606 | 0.00606 | 0.0025 | 0.0025 | 0.0025 | 0.46508 | 5.5976 | 214.272 | 0.03 | 1716 | 6570 | 6949 | 7349
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00384 | 0.0025 | 0.006465 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.006 | 0.006 | 0.0025 | 0.0025 | 0.0025 | 0.46657 | 5.6065 | 214.272 | 0.03 | 1713 | 6558 | 6936 | 7337
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003795 | 0.0025 | 0.00639 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00594 | 0.00594 | 0.0025 | 0.0025 | 0.0025 | 0.46807 | 5.6155 | 214.272 | 0.03 | 1709 | 6546 | 6924 | 7324
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003765 | 0.0025 | 0.00633 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00588 | 0.00588 | 0.0025 | 0.0025 | 0.0025 | 0.46988 | 5.6264 | 214.272 | 0.03 | 1706 | 6533 | 6912 | 7312
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005925 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005505 | 0.005505 | 0.0025 | 0.0025 | 0.0025 | 0.47425 | 5.4903 | 228.672 | 0.03 | 1646 | 6287 | 6642 | 7017
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005865 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005445 | 0.005445 | 0.0025 | 0.0025 | 0.0025 | 0.47733 | 6.0879 | 228.672 | 0.03 | 1457 | 5532 | 5975 | 6350
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005805 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005385 | 0.005385 | 0.0025 | 0.0025 | 0.0025 | 0.48087 | 6.1104 | 228.672 | 0.03 | 1451 | 5491 | 5954 | 6329
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005745 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.005325 | 0.005325 | 0.0025 | 0.0025 | 0.0025 | 0.48467 | 6.1345 | 228.672 | 0.03 | 1446 | 5451 | 5934 | 6309
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005685 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00528 | 0.00528 | 0.0025 | 0.0025 | 0.0025 | 0.48909 | 6.1624 | 228.672 | 0.03 | 1437 | 5390 | 5903 | 6278
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00537 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00498 | 0.00498 | 0.0025 | 0.0025 | 0.0025 | 0.51379 | 6.1061 | 243.072 | 0.03 | 1365 | 5166 | 5601 | 5954
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00531 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004935 | 0.004935 | 0.0025 | 0.0025 | 0.0025 | 0.52178 | 6.8012 | 243.072 | 0.03 | 1200 | 3847 | 4990 | 5341
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00525 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004875 | 0.004875 | 0.0025 | 0.0025 | 0.0025 | 0.53167 | 6.8653 | 243.072 | 0.03 | 1185 | 3713 | 4933 | 5284
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005205 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00483 | 0.00483 | 0.0025 | 0.0025 | 0.0025 | 0.54338 | 6.9405 | 243.072 | 0.03 | 1170 | 3579 | 4877 | 5228
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.005145 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004785 | 0.004785 | 0.0025 | 0.0025 | 0.0025 | 0.55818 | 7.0344 | 243.072 | 0.03 | 1152 | 3407 | 4784 | 5157
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004905 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004545 | 0.004545 | 0.0025 | 0.0025 | 0.0025 | 0.60864 | 7.0721 | 257.472 | 0.03 | 1080 | 3145 | 4458 | 4839
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004845 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.0045 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.63379 | 7.9764 | 257.472 | 0.03 | 927 | 1502 | 3139 | 4235
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0048 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004455 | 0.004455 | 0.0025 | 0.0025 | 0.0025 | 0.64493 | 8.0462 | 257.472 | 0.03 | 916 | 1455 | 3037 | 4164
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004755 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00441 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.6482 | 8.0665 | 257.472 | 0.03 | 913 | 1451 | 3008 | 4140
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004695 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004365 | 0.004365 | 0.0025 | 0.0025 | 0.0025 | 0.65187 | 8.0894 | 257.472 | 0.03 | 910 | 1446 | 2980 | 4116
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.0045 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004185 | 0.004185 | 0.0025 | 0.0025 | 0.0025 | 0.66946 | 7.8641 | 271.872 | 0.03 | 895 | 1627 | 3138 | 4080
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004455 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00414 | 0.00414 | 0.0025 | 0.0025 | 0.0025 | 0.67602 | 8.7344 | 271.872 | 0.03 | 781 | 1249 | 1943 | 3177
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00441 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004095 | 0.004095 | 0.0025 | 0.0025 | 0.0025 | 0.68412 | 8.7866 | 271.872 | 0.03 | 774 | 1238 | 1860 | 3110
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.004365 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.00405 | 0.00405 | 0.0025 | 0.0025 | 0.0025 | 0.69369 | 8.8478 | 271.872 | 0.03 | 767 | 1228 | 1778 | 3042
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.0025 | 0.0025 | 0.00432 | 0.0025 | 0.0025 | 0.0025 | 0.0025 | 0.004005 | 0.004005 | 0.0025 | 0.0025 | 0.0025 | 0.6164 | 8.7946 | 272.816 | 0.03 | 771 | 1234 | 1853 | 3099

## Rho_25%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0041875 | 0.0034875 | 0.00705 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0065375 | 0.0065375 | 0.003125 | 0.003125 | 0.003125 | 0.45227 | 4.2599 | 185.472 | 0.03 | 2696 | 9951 | 10384 | 10836
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00415 | 0.00345 | 0.006975 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.006475 | 0.006475 | 0.003125 | 0.003125 | 0.003125 | 0.45255 | 4.7097 | 185.472 | 0.03 | 2414 | 9047 | 9483 | 9941
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0041 | 0.003425 | 0.0069 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0064125 | 0.0064125 | 0.003125 | 0.003125 | 0.003125 | 0.45282 | 4.7111 | 185.472 | 0.03 | 2414 | 9047 | 9483 | 9941
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0040625 | 0.003375 | 0.006825 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00635 | 0.00635 | 0.003125 | 0.003125 | 0.003125 | 0.45315 | 4.7128 | 185.472 | 0.03 | 2414 | 9047 | 9483 | 9941
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0040125 | 0.00335 | 0.00675 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.006275 | 0.006275 | 0.003125 | 0.003125 | 0.003125 | 0.45347 | 4.7145 | 185.472 | 0.03 | 2414 | 9047 | 9483 | 9941
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003675 | 0.003125 | 0.0061875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00575 | 0.00575 | 0.003125 | 0.003125 | 0.003125 | 0.45887 | 4.6606 | 199.872 | 0.03 | 2267 | 8483 | 8887 | 9311
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036375 | 0.003125 | 0.006125 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0056875 | 0.0056875 | 0.003125 | 0.003125 | 0.003125 | 0.45958 | 5.1552 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036 | 0.003125 | 0.0060625 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.005625 | 0.005625 | 0.003125 | 0.003125 | 0.003125 | 0.46042 | 5.1599 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0035625 | 0.003125 | 0.006 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.005575 | 0.005575 | 0.003125 | 0.003125 | 0.003125 | 0.46133 | 5.165 | 199.872 | 0.03 | 2017 | 7653 | 8059 | 8487
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003525 | 0.003125 | 0.005925 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0055125 | 0.0055125 | 0.003125 | 0.003125 | 0.003125 | 0.46228 | 5.1704 | 199.872 | 0.03 | 2017 | 7653 | 8059 | 8487
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.003675 | 0.003125 | 0.0061875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00575 | 0.00575 | 0.003125 | 0.003125 | 0.003125 | 0.45887 | 4.6606 | 199.872 | 0.03 | 2267 | 8483 | 8887 | 9311
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036375 | 0.003125 | 0.006125 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0056875 | 0.0056875 | 0.003125 | 0.003125 | 0.003125 | 0.45958 | 5.1552 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0036 | 0.003125 | 0.0060625 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.005625 | 0.005625 | 0.003125 | 0.003125 | 0.003125 | 0.46042 | 5.1599 | 199.872 | 0.03 | 2022 | 7668 | 8074 | 8502
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031625 | 0.003125 | 0.005325 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00495 | 0.00495 | 0.003125 | 0.003125 | 0.003125 | 0.47578 | 5.6616 | 214.272 | 0.03 | 1695 | 6496 | 6875 | 7275
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031375 | 0.003125 | 0.005275 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0049 | 0.0049 | 0.003125 | 0.003125 | 0.003125 | 0.47787 | 5.674 | 214.272 | 0.03 | 1692 | 6484 | 6863 | 7263
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032625 | 0.003125 | 0.0055 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0051 | 0.0051 | 0.003125 | 0.003125 | 0.003125 | 0.47073 | 5.0951 | 214.272 | 0.03 | 1911 | 7238 | 7617 | 8015
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032375 | 0.003125 | 0.0054375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00505 | 0.00505 | 0.003125 | 0.003125 | 0.003125 | 0.47228 | 5.6407 | 214.272 | 0.03 | 1702 | 6521 | 6899 | 7300
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0032 | 0.003125 | 0.0053875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.005 | 0.005 | 0.003125 | 0.003125 | 0.003125 | 0.47402 | 5.6511 | 214.272 | 0.03 | 1699 | 6509 | 6887 | 7287
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031625 | 0.003125 | 0.005325 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00495 | 0.00495 | 0.003125 | 0.003125 | 0.003125 | 0.47578 | 5.6616 | 214.272 | 0.03 | 1695 | 6496 | 6875 | 7275
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.0031375 | 0.003125 | 0.005275 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0049 | 0.0049 | 0.003125 | 0.003125 | 0.003125 | 0.47787 | 5.674 | 214.272 | 0.03 | 1692 | 6484 | 6863 | 7263
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0049375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0045875 | 0.0045875 | 0.003125 | 0.003125 | 0.003125 | 0.4926 | 5.5955 | 228.672 | 0.03 | 1608 | 6157 | 6511 | 6886
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0048875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0045375 | 0.0045375 | 0.003125 | 0.003125 | 0.003125 | 0.496 | 6.2058 | 228.672 | 0.03 | 1424 | 5288 | 5853 | 6228
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0048375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0044875 | 0.0044875 | 0.003125 | 0.003125 | 0.003125 | 0.4999 | 6.2301 | 228.672 | 0.03 | 1418 | 5248 | 5833 | 6208
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0047875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0044375 | 0.0044375 | 0.003125 | 0.003125 | 0.003125 | 0.50403 | 6.2559 | 228.672 | 0.03 | 1410 | 5187 | 5803 | 6178
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0047375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0044 | 0.0044 | 0.003125 | 0.003125 | 0.003125 | 0.5088 | 6.2854 | 228.672 | 0.03 | 1402 | 5126 | 5774 | 6149
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.004475 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00415 | 0.00415 | 0.003125 | 0.003125 | 0.003125 | 0.53488 | 6.2302 | 243.072 | 0.03 | 1334 | 4936 | 5488 | 5840
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.004425 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0041125 | 0.0041125 | 0.003125 | 0.003125 | 0.003125 | 0.54301 | 6.9381 | 243.072 | 0.03 | 1170 | 3579 | 4877 | 5228
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.004375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0040625 | 0.0040625 | 0.003125 | 0.003125 | 0.003125 | 0.55287 | 7.0008 | 243.072 | 0.03 | 1158 | 3464 | 4830 | 5181
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0043375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.004025 | 0.004025 | 0.003125 | 0.003125 | 0.003125 | 0.56424 | 7.0725 | 243.072 | 0.03 | 1144 | 3331 | 4722 | 5126
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0042875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0039875 | 0.0039875 | 0.003125 | 0.003125 | 0.003125 | 0.57823 | 7.1596 | 243.072 | 0.03 | 1126 | 3159 | 4584 | 5057
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0040875 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0037875 | 0.0037875 | 0.003125 | 0.003125 | 0.003125 | 0.62569 | 7.1705 | 257.472 | 0.03 | 1061 | 2964 | 4314 | 4767
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0040375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00375 | 0.00375 | 0.003125 | 0.003125 | 0.003125 | 0.64741 | 8.0616 | 257.472 | 0.03 | 915 | 1453 | 3023 | 4152
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.004 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0037125 | 0.0037125 | 0.003125 | 0.003125 | 0.003125 | 0.65718 | 8.1223 | 257.472 | 0.03 | 906 | 1440 | 2936 | 4080
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0039625 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.003675 | 0.003675 | 0.003125 | 0.003125 | 0.003125 | 0.66066 | 8.1437 | 257.472 | 0.03 | 903 | 1436 | 2907 | 4056
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0039125 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0036375 | 0.0036375 | 0.003125 | 0.003125 | 0.003125 | 0.66453 | 8.1676 | 257.472 | 0.03 | 899 | 1429 | 2864 | 4021
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.00375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0034875 | 0.0034875 | 0.003125 | 0.003125 | 0.003125 | 0.68258 | 7.9408 | 271.872 | 0.03 | 883 | 1491 | 3028 | 4034
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0037125 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.00345 | 0.00345 | 0.003125 | 0.003125 | 0.003125 | 0.68908 | 8.8183 | 271.872 | 0.03 | 770 | 1233 | 1819 | 3076
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.003675 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0034125 | 0.0034125 | 0.003125 | 0.003125 | 0.003125 | 0.69695 | 8.8685 | 271.872 | 0.03 | 765 | 1224 | 1751 | 3020
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0036375 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.003375 | 0.003375 | 0.003125 | 0.003125 | 0.003125 | 0.70603 | 8.9262 | 271.872 | 0.03 | 758 | 1214 | 1668 | 2952
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.003125 | 0.003125 | 0.0036 | 0.003125 | 0.003125 | 0.003125 | 0.003125 | 0.0033375 | 0.0033375 | 0.003125 | 0.003125 | 0.003125 | 0.63211 | 8.9059 | 272.816 | 0.03 | 758 | 1214 | 1689 | 2964

## Rho_50%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.005025 | 0.004185 | 0.00846 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.007845 | 0.007845 | 0.00375 | 0.00375 | 0.00375 | 0.47203 | 4.3519 | 185.472 | 0.03 | 2636 | 9759 | 10193 | 10646
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00498 | 0.00414 | 0.00837 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00777 | 0.00777 | 0.00375 | 0.00375 | 0.00375 | 0.47233 | 4.8115 | 185.472 | 0.03 | 2358 | 8863 | 9300 | 9759
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00492 | 0.00411 | 0.00828 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.007695 | 0.007695 | 0.00375 | 0.00375 | 0.00375 | 0.47262 | 4.813 | 185.472 | 0.03 | 2358 | 8863 | 9300 | 9759
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.004875 | 0.00405 | 0.00819 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00762 | 0.00762 | 0.00375 | 0.00375 | 0.00375 | 0.47299 | 4.8149 | 185.472 | 0.03 | 2358 | 8863 | 9300 | 9759
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.004815 | 0.00402 | 0.0081 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00753 | 0.00753 | 0.00375 | 0.00375 | 0.00375 | 0.47333 | 4.8166 | 185.472 | 0.03 | 2353 | 8845 | 9282 | 9741
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.00375 | 0.007425 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0069 | 0.0069 | 0.00375 | 0.00375 | 0.00375 | 0.47935 | 4.7635 | 199.872 | 0.03 | 2214 | 8310 | 8715 | 9139
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004365 | 0.00375 | 0.00735 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.006825 | 0.006825 | 0.00375 | 0.00375 | 0.00375 | 0.48012 | 5.2691 | 199.872 | 0.03 | 1974 | 7505 | 7911 | 8339
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.00375 | 0.007275 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00675 | 0.00675 | 0.00375 | 0.00375 | 0.00375 | 0.48103 | 5.2741 | 199.872 | 0.03 | 1974 | 7505 | 7911 | 8339
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004275 | 0.00375 | 0.0072 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00669 | 0.00669 | 0.00375 | 0.00375 | 0.00375 | 0.48203 | 5.2796 | 199.872 | 0.03 | 1969 | 7490 | 7896 | 8324
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00423 | 0.00375 | 0.00711 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.006615 | 0.006615 | 0.00375 | 0.00375 | 0.00375 | 0.48307 | 5.2853 | 199.872 | 0.03 | 1965 | 7475 | 7881 | 8310
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00441 | 0.00375 | 0.007425 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0069 | 0.0069 | 0.00375 | 0.00375 | 0.00375 | 0.47935 | 4.7635 | 199.872 | 0.03 | 2214 | 8310 | 8715 | 9139
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.004365 | 0.00375 | 0.00735 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.006825 | 0.006825 | 0.00375 | 0.00375 | 0.00375 | 0.48012 | 5.2691 | 199.872 | 0.03 | 1974 | 7505 | 7911 | 8339
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00432 | 0.00375 | 0.007275 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00675 | 0.00675 | 0.00375 | 0.00375 | 0.00375 | 0.48103 | 5.2741 | 199.872 | 0.03 | 1974 | 7505 | 7911 | 8339
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003795 | 0.00375 | 0.00639 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00594 | 0.00594 | 0.00375 | 0.00375 | 0.00375 | 0.49777 | 5.791 | 214.272 | 0.03 | 1651 | 6340 | 6718 | 7119
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003765 | 0.00375 | 0.00633 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00588 | 0.00588 | 0.00375 | 0.00375 | 0.00375 | 0.50002 | 5.804 | 214.272 | 0.03 | 1647 | 6328 | 6706 | 7107
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003915 | 0.00375 | 0.0066 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00612 | 0.00612 | 0.00375 | 0.00375 | 0.00375 | 0.49233 | 5.2107 | 214.272 | 0.03 | 1865 | 7083 | 7462 | 7861
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003885 | 0.00375 | 0.006525 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00606 | 0.00606 | 0.00375 | 0.00375 | 0.00375 | 0.494 | 5.769 | 214.272 | 0.03 | 1657 | 6364 | 6742 | 7142
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00384 | 0.00375 | 0.006465 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.006 | 0.006 | 0.00375 | 0.00375 | 0.00375 | 0.49589 | 5.78 | 214.272 | 0.03 | 1654 | 6352 | 6730 | 7130
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003795 | 0.00375 | 0.00639 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00594 | 0.00594 | 0.00375 | 0.00375 | 0.00375 | 0.49777 | 5.791 | 214.272 | 0.03 | 1651 | 6340 | 6718 | 7119
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.003765 | 0.00375 | 0.00633 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00588 | 0.00588 | 0.00375 | 0.00375 | 0.00375 | 0.50002 | 5.804 | 214.272 | 0.03 | 1647 | 6328 | 6706 | 7107
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005925 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.005505 | 0.005505 | 0.00375 | 0.00375 | 0.00375 | 0.51589 | 5.7262 | 228.672 | 0.03 | 1566 | 6008 | 6362 | 6737
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005865 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.005445 | 0.005445 | 0.00375 | 0.00375 | 0.00375 | 0.51949 | 6.351 | 228.672 | 0.03 | 1386 | 5004 | 5716 | 6090
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005805 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.005385 | 0.005385 | 0.00375 | 0.00375 | 0.00375 | 0.52359 | 6.376 | 228.672 | 0.03 | 1378 | 4943 | 5687 | 6061
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005745 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.005325 | 0.005325 | 0.00375 | 0.00375 | 0.00375 | 0.52792 | 6.4024 | 228.672 | 0.03 | 1373 | 4902 | 5668 | 6042
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005685 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00528 | 0.00528 | 0.00375 | 0.00375 | 0.00375 | 0.53289 | 6.4324 | 228.672 | 0.03 | 1365 | 4841 | 5639 | 6014
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00537 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00498 | 0.00498 | 0.00375 | 0.00375 | 0.00375 | 0.55963 | 6.3727 | 243.072 | 0.03 | 1299 | 4669 | 5359 | 5711
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00531 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004935 | 0.004935 | 0.00375 | 0.00375 | 0.00375 | 0.56772 | 7.0942 | 243.072 | 0.03 | 1140 | 3292 | 4692 | 5111
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00525 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004875 | 0.004875 | 0.00375 | 0.00375 | 0.00375 | 0.57738 | 7.1544 | 243.072 | 0.03 | 1128 | 3178 | 4600 | 5065
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005205 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00483 | 0.00483 | 0.00375 | 0.00375 | 0.00375 | 0.58832 | 7.2218 | 243.072 | 0.03 | 1114 | 3044 | 4492 | 5012
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.005145 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004785 | 0.004785 | 0.00375 | 0.00375 | 0.00375 | 0.60151 | 7.3023 | 243.072 | 0.03 | 1099 | 2891 | 4369 | 4953
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004905 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004545 | 0.004545 | 0.00375 | 0.00375 | 0.00375 | 0.64614 | 7.2867 | 257.472 | 0.03 | 1039 | 2748 | 4140 | 4683
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004845 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.0045 | 0.0045 | 0.00375 | 0.00375 | 0.00375 | 0.66529 | 8.1722 | 257.472 | 0.03 | 899 | 1429 | 2864 | 4021
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0048 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004455 | 0.004455 | 0.00375 | 0.00375 | 0.00375 | 0.67408 | 8.226 | 257.472 | 0.03 | 891 | 1417 | 2776 | 3949
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004755 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00441 | 0.00441 | 0.00375 | 0.00375 | 0.00375 | 0.67764 | 8.2478 | 257.472 | 0.03 | 888 | 1412 | 2748 | 3926
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004695 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004365 | 0.004365 | 0.00375 | 0.00375 | 0.00375 | 0.68158 | 8.2717 | 257.472 | 0.03 | 885 | 1408 | 2719 | 3902
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.0045 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004185 | 0.004185 | 0.00375 | 0.00375 | 0.00375 | 0.69965 | 8.0395 | 271.872 | 0.03 | 869 | 1380 | 2891 | 3955
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004455 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00414 | 0.00414 | 0.00375 | 0.00375 | 0.00375 | 0.70597 | 8.9258 | 271.872 | 0.03 | 758 | 1214 | 1668 | 2952
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00441 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004095 | 0.004095 | 0.00375 | 0.00375 | 0.00375 | 0.71351 | 8.9733 | 271.872 | 0.03 | 753 | 1208 | 1613 | 2907
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.004365 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.00405 | 0.00405 | 0.00375 | 0.00375 | 0.00375 | 0.72206 | 9.0269 | 271.872 | 0.03 | 747 | 1198 | 1565 | 2839
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.00375 | 0.00375 | 0.00432 | 0.00375 | 0.00375 | 0.00375 | 0.00375 | 0.004005 | 0.004005 | 0.00375 | 0.00375 | 0.00375 | 0.65056 | 9.035 | 272.816 | 0.03 | 744 | 1194 | 1560 | 2829

## Rho_100%
| l1 | l2 | bay1 | bay2 | c1 | c2 | ν | f'c | fy | h | wc | SDL | LL | LLvib | l1 | l1 | l1 | l1 | l1 | l1 | l2 | l2 | l2 | l2 | l2 | l2 | k1 | fn | W | b | Very Slow | Slow | Moderate | Fast
Slab_ID | ft | ft | type | type | in | in |  | psi | psi | in | pcf | psf | psf | psf | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | rcol,p | rcol,n1 | rcol,n2 | rmid,p | rmid,n1 | rmid,n2 | cracking factor | Hz | kips | % | mips | mips | mips | mips
1 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0067 | 0.00558 | 0.01128 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01046 | 0.01046 | 0.005 | 0.005 | 0.005 | 0.50861 | 4.5174 | 185.472 | 0.03 | 2527 | 9412 | 9848 | 10303
2 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00664 | 0.00552 | 0.01116 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01036 | 0.01036 | 0.005 | 0.005 | 0.005 | 0.50893 | 4.9945 | 185.472 | 0.03 | 2263 | 8547 | 8984 | 9444
3 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00656 | 0.00548 | 0.01104 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01026 | 0.01026 | 0.005 | 0.005 | 0.005 | 0.50926 | 4.9961 | 185.472 | 0.03 | 2258 | 8530 | 8967 | 9427
4 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.0065 | 0.0054 | 0.01092 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01016 | 0.01016 | 0.005 | 0.005 | 0.005 | 0.50965 | 4.998 | 185.472 | 0.03 | 2258 | 8530 | 8967 | 9427
5 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 12 | 150 | 0 | 80 | 11 | 0.00642 | 0.00536 | 0.0108 | 0.005 | 0.005 | 0.005 | 0.005 | 0.01004 | 0.01004 | 0.005 | 0.005 | 0.005 | 0.51002 | 4.9998 | 185.472 | 0.03 | 2258 | 8530 | 8967 | 9427
6 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00588 | 0.005 | 0.0099 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0092 | 0.0092 | 0.005 | 0.005 | 0.005 | 0.51701 | 4.9471 | 199.872 | 0.03 | 2119 | 7995 | 8401 | 8827
7 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00582 | 0.005 | 0.0098 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0091 | 0.0091 | 0.005 | 0.005 | 0.005 | 0.51787 | 5.4724 | 199.872 | 0.03 | 1891 | 7220 | 7626 | 8055
8 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00576 | 0.005 | 0.0097 | 0.005 | 0.005 | 0.005 | 0.005 | 0.009 | 0.009 | 0.005 | 0.005 | 0.005 | 0.51887 | 5.4777 | 199.872 | 0.03 | 1887 | 7206 | 7612 | 8041
9 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.0057 | 0.005 | 0.0096 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00892 | 0.00892 | 0.005 | 0.005 | 0.005 | 0.51998 | 5.4835 | 199.872 | 0.03 | 1887 | 7206 | 7612 | 8041
10 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00564 | 0.005 | 0.00948 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00882 | 0.00882 | 0.005 | 0.005 | 0.005 | 0.52113 | 5.4896 | 199.872 | 0.03 | 1883 | 7193 | 7599 | 8027
11 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00588 | 0.005 | 0.0099 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0092 | 0.0092 | 0.005 | 0.005 | 0.005 | 0.51701 | 4.9471 | 199.872 | 0.03 | 2119 | 7995 | 8401 | 8827
12 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00582 | 0.005 | 0.0098 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0091 | 0.0091 | 0.005 | 0.005 | 0.005 | 0.51787 | 5.4724 | 199.872 | 0.03 | 1891 | 7220 | 7626 | 8055
13 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 13 | 150 | 0 | 80 | 11 | 0.00576 | 0.005 | 0.0097 | 0.005 | 0.005 | 0.005 | 0.005 | 0.009 | 0.009 | 0.005 | 0.005 | 0.005 | 0.51887 | 5.4777 | 199.872 | 0.03 | 1887 | 7206 | 7612 | 8041
14 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00506 | 0.005 | 0.00852 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00792 | 0.00792 | 0.005 | 0.005 | 0.005 | 0.53751 | 6.0177 | 214.272 | 0.03 | 1576 | 6056 | 6454 | 6854
15 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00502 | 0.005 | 0.00844 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00784 | 0.00784 | 0.005 | 0.005 | 0.005 | 0.53994 | 6.0313 | 214.272 | 0.03 | 1573 | 6034 | 6442 | 6843
16 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00522 | 0.005 | 0.0088 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00816 | 0.00816 | 0.005 | 0.005 | 0.005 | 0.53159 | 5.4145 | 214.272 | 0.03 | 1786 | 6813 | 7192 | 7592
17 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00518 | 0.005 | 0.0087 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00808 | 0.00808 | 0.005 | 0.005 | 0.005 | 0.53342 | 5.9948 | 214.272 | 0.03 | 1586 | 6110 | 6487 | 6888
18 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00512 | 0.005 | 0.00862 | 0.005 | 0.005 | 0.005 | 0.005 | 0.008 | 0.008 | 0.005 | 0.005 | 0.005 | 0.53547 | 6.0062 | 214.272 | 0.03 | 1580 | 6077 | 6465 | 6865
19 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00506 | 0.005 | 0.00852 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00792 | 0.00792 | 0.005 | 0.005 | 0.005 | 0.53751 | 6.0177 | 214.272 | 0.03 | 1576 | 6056 | 6454 | 6854
20 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 14 | 150 | 0 | 80 | 11 | 0.00502 | 0.005 | 0.00844 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00784 | 0.00784 | 0.005 | 0.005 | 0.005 | 0.53994 | 6.0313 | 214.272 | 0.03 | 1573 | 6034 | 6442 | 6843
21 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.0079 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00734 | 0.00734 | 0.005 | 0.005 | 0.005 | 0.55734 | 5.9518 | 228.672 | 0.03 | 1498 | 5767 | 6121 | 6496
22 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00782 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00726 | 0.00726 | 0.005 | 0.005 | 0.005 | 0.56114 | 6.6008 | 228.672 | 0.03 | 1323 | 4496 | 5482 | 5856
23 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00774 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00718 | 0.00718 | 0.005 | 0.005 | 0.005 | 0.56546 | 6.6261 | 228.672 | 0.03 | 1315 | 4435 | 5454 | 5828
24 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00766 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0071 | 0.0071 | 0.005 | 0.005 | 0.005 | 0.56996 | 6.6524 | 228.672 | 0.03 | 1311 | 4394 | 5436 | 5810
25 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 15 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00758 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00704 | 0.00704 | 0.005 | 0.005 | 0.005 | 0.5751 | 6.6823 | 228.672 | 0.03 | 1303 | 4333 | 5410 | 5783
26 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00716 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00664 | 0.00664 | 0.005 | 0.005 | 0.005 | 0.60216 | 6.6104 | 243.072 | 0.03 | 1242 | 4210 | 5148 | 5500
27 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00708 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00658 | 0.00658 | 0.005 | 0.005 | 0.005 | 0.60994 | 7.3533 | 243.072 | 0.03 | 1089 | 2795 | 4292 | 4916
28 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.007 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0065 | 0.0065 | 0.005 | 0.005 | 0.005 | 0.61905 | 7.408 | 243.072 | 0.03 | 1078 | 2681 | 4200 | 4873
29 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00694 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00644 | 0.00644 | 0.005 | 0.005 | 0.005 | 0.6291 | 7.4679 | 243.072 | 0.03 | 1068 | 2566 | 4108 | 4830
30 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 16 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00686 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00638 | 0.00638 | 0.005 | 0.005 | 0.005 | 0.64087 | 7.5375 | 243.072 | 0.03 | 1055 | 2432 | 4001 | 4781
31 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00654 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00606 | 0.00606 | 0.005 | 0.005 | 0.005 | 0.68064 | 7.4787 | 257.472 | 0.03 | 1006 | 2405 | 3864 | 4553
32 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00646 | 0.005 | 0.005 | 0.005 | 0.005 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.69618 | 8.3598 | 257.472 | 0.03 | 873 | 1390 | 2588 | 3795
33 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.0064 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00594 | 0.00594 | 0.005 | 0.005 | 0.005 | 0.70364 | 8.4045 | 257.472 | 0.03 | 867 | 1382 | 2530 | 3747
34 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00634 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00588 | 0.00588 | 0.005 | 0.005 | 0.005 | 0.70722 | 8.4258 | 257.472 | 0.03 | 863 | 1376 | 2487 | 3712
35 | 36 | 32 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 17 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00626 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00582 | 0.00582 | 0.005 | 0.005 | 0.005 | 0.71113 | 8.4491 | 257.472 | 0.03 | 860 | 1372 | 2458 | 3688
36 | 36 | 32 | exterior | interior | 24 | 24 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.006 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00558 | 0.00558 | 0.005 | 0.005 | 0.005 | 0.72869 | 8.2046 | 271.872 | 0.03 | 847 | 1348 | 2671 | 3775
37 | 36 | 32 | exterior | interior | 26 | 26 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00594 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00552 | 0.00552 | 0.005 | 0.005 | 0.005 | 0.73453 | 9.1045 | 271.872 | 0.03 | 739 | 1186 | 1551 | 2760
38 | 36 | 32 | exterior | interior | 28 | 28 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00588 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00546 | 0.00546 | 0.005 | 0.005 | 0.005 | 0.74135 | 9.1467 | 271.872 | 0.03 | 734 | 1178 | 1541 | 2704
39 | 36 | 32 | exterior | interior | 30 | 30 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00582 | 0.005 | 0.005 | 0.005 | 0.005 | 0.0054 | 0.0054 | 0.005 | 0.005 | 0.005 | 0.7489 | 9.1931 | 271.872 | 0.03 | 729 | 1172 | 1533 | 2659
40 | 34 | 34 | exterior | interior | 32 | 32 | 0.2 | 5000 | 60000 | 18 | 150 | 0 | 80 | 11 | 0.005 | 0.005 | 0.00576 | 0.005 | 0.005 | 0.005 | 0.005 | 0.00534 | 0.00534 | 0.005 | 0.005 | 0.005 | 0.68312 | 9.2583 | 272.816 | 0.03 | 720 | 1157 | 1514 | 2571